## LLS_Energy_Losses___Unaccounte
OPC 012978
FPL RC-16
| (1) | (2) | (3) | (4)
Line No. | LLS - Energy Losses & Unaccounted For Energy | Losses (MWH) | Sales (MWH) | Net Energy (MWH)
1 | Net Energy to Transmission (a) | 0 | 0 | 126985912.6915
2
3 | Generation Step-Up Transformer Losses (b) | 234835.5486 | 0 | -234835.5486
4 | Southern JEA / Transfers Loss Payback (c) | 151224 | 0 | 0
5 | Adjusted Transmission Line & Substation Losses (d) | 2040649.6276 | 0 | -2040649.6276
6
7 | Distribution Substation Transformer Losses (e) | 460540.3532 | 0 | -460540.3532
8
9 | Other Distribution & Unaccounted For: |  | 0 | 0
10 | Primary Line Losses (f) | 568396.5565 | 0 | 0
11
12 | Transformer Losses (g) | 1916029.7285 | 0 | 0
13
14 | Secondary & Service Losses (h) | 308309.9067 | 0 | 0
15
16 | Subtotal - Distribution & Unaccounted For | 2792736.1917 | 0 | -2792736.1917
17
18 | Total Losses & Unaccounted For (i) | 5528761.721 | 0 | 0
19
20 | System Energy Net of Losses and Unaccounted For | 0 | 0 | 121457150.9705
21
22 | ---- Delivered Sales ---- |  | 0 | 0
23 | Retail Transmission (j) | 0 | 1738682.4265 | 0
24 | Primary (k) | 0 | 2479984.651 | 0
25 | Secondary (l) | 0 | 103210101.0183 | 0
26 | Total Retail (m) | 0 | 107428768.0959 | 0
27
28 | Wholesale Transmission (n) | 0 | 6535642.639 | 0
29 | Primary (o) | 0 | 1e-06 | 0
30 | Total Resale (p) | 0 | 6535642.639 | 0
31
32 | Total Delivered Sales (q) | 0 | 0 | -113964410.7348
33
34 | Company Use (r) | 0 | 0 | -131587.2357
35
36 | Less (Seminole + Firm Wheeling) - Southern JEA LP + Non-firm Wheeling Losses (s) | 0 | 0 | -7361153
37
38 | Total | 0 | 0 | -9.6112e-07
39
1 | (a) Power Supply
2 | (b) Power Supply
3 | (c) Power Supply
4 | (d) Power Supply
5 | (e) Power Supply
6 | (f) Primary line losses are estimated using the methodology provided by Distribution Engineering.
7 | (g) Transformer losses are estimated using the methodology provided by Distribution Engineering.
8 | (h) Secondary and service losses include electricity theft and unknown usage (UKU)
9 | (i) Net Energy for Load (NEL) - Delivered Sales - Company Use
10 | (j) Total company's retail delivered transmission energy sales from Rate Load Research study.
11 | (k) Total company's retail delivered primary energy sales from Rate Load Research study.
12 | (l) Total company's retail delivered secondary energy sales from Rate Load Research study.
13 | (m) Sum of (J), (K), and (L). Also see Financial and Operating Report, page 8-A, 1 of 2, line 36
14 | (n) Total company's wholesale delivered transmission energy sales from Rate Load Research study.
15 | (o) Total company's wholesale delivered primary energy sales form Rate Load Research study.
16 | (p) Sum of (N) and (O). Also see Financial and Operating Report, page 8-A, 1 of 2, line 39
17 | (q) Sum of (M) and (P). Also see Financial and Operating Report, page 8-A, 1 of 2, line 40
18 | (r) FERC Form 1, Page 401a
19 | (s) Power Supply
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39

## LLS_Loss_Expansion_Factors_Sum
OPC 012979
FPL RC-16
Line No. | Voltage Level |  | Energy Expansion Factor | Demand Expansion Factor | Loss %
1
2 | Transmission | 0 | 1.017 | 1.0216 | 1.673%
3
4 | Primary | 0 | 1.0267 | 1.0345 | 2.6%
5
6 | Secondary | 0 | 1.0488 | 1.064 | 4.653%
7
8
9 | Company Use Demand: |  | 0 | 0 | 0%
10 | (GSD-1) 12CP | 4000518.8206 | 0 | 0 | 0%
11 | (GSD-1) KWH | 25829102.0078 | 0 | 0 | 0%
12 | Load Factor | 0.73704 | 0 | 0 | 0%
13 | 12CP Demand (rounded) | 20.3808 | 0 | 0 | 0%
14
15
16 | Calculation Net Energy to Transmission Less Southern JEA LP: |  | 0 | 0 | 0%
17 | Net Energy For Load | 119624759.6915 | 0 | 0 | 0%
18
19 | + Seminole Load Received | 2282100 | 0 | 0 | 0%
20 | + St. Lucie Entitlement Received | 586976 | 0 | 0 | 0%
21 | + Power wheeled for others | 4643301 | 0 | 0 | 0%
22 | - Southern JEA / Transfers Loss Payback | -19451 | 0 | 0 | 0%
23 | - Non-Firm Wheeling Losses | -77259 | 0 | 0 | 0%
24 | - Short Term Firm Wheeling Losses | -54514 | 0 | 0 | 0%
25 | Seminole + Firm Wheeling - Southern JEA LP | 7361153 | 0 | 0 | 0%
26
27 | Net Energy To Transmission Less Southern JEA LP | 126985912.6915 | 0 | 0 | 0%
28
29
30 | USING UNBILLED SALES |  | 0 | 0 | 0%
31 | NEL | 119624759.6915 | 0 | 0 | 0%
32 | PRIOR MONTH UNBILLED | 4138704.6983 | 0 | 0 | 0%
33 | SUBTOTAL | 123763464.3899 | 0 | 0 | 0%
34 | BILLED SALES | -113898210.6407 | 0 | 0 | 0%
35 | COMPANY USE | -131587.2357 | 0 | 0 | 0%
36 | CURRENT MONTH UNBILLED | -4204904.7925 | 0 | 0 | 0%
37 | ENERGY LOST OR UNACCOUNTED FOR | 5528761.721 | 0 | 0 | 0%
38 | % LOST OR UNACCOUNTED FOR | 4.622% | 0 | 0 | 0%
39
40
41 | OVERALL UNBILLED FACTOR |  | 0 | 0 | 0%
42 | TOTAL DELIVERED MWH | 113964410.7348 | 0 | 0 | 0%
43 | TOTAL BILLED MWH | 113898210.6423 | 0 | 0 | 0%
44 | TOTAL UNBILLED FACTOR | 1.0006 | 0 | 0 | 0%

## LLS_Loss_Expansion_Factors_Ene
OPC 012980
FPL RC-16
| (1) | (2) | (3) | (4) | (5) | (6)
Line No. |  | Flow MWH | Loss % | Loss Multiplier | Expansion Factor | Cumulative Loss %
1 | Net Energy to Transmission | 126985912.6915 | 0% | 0 | 0 | 0%
2
3 | Generation Step-up Transformer Losses | -234835.5486 | 0.1849% | 1.0019 | 0 | 0%
4
5 | Flow to Transmission | 126751077.143 | 0% | 0 | 0 | 0%
6
7 | Transmission Line & Substation Losses | -2040649.6276 | 0% | 0 | 0 | 0%
8
9 | Remove JEA/Southern LP, NF & STF Wheeling Losses (1) | -151224 | 0% | 0 | 0 | 0%
10
11 | Adjusted Transmission Line & Substation Losses | -1889425.6276 | 1.491% | 1.0151 | 0 | 0%
12
13 | Flow on Transmission | 124861651.5154 | 0% | 0 | 0 | 0%
14
15 | Delivered Sales at Transmission | -8274325.0655 | 0% | 0 | 1.017 | 1.673%
16
17 | Seminole & Firm Power Wheeled for Others | -7361153 | 0% | 0 | 0 | 0%
18
19 | Include JEA/Southern LP, NF & STF Wheeling Losses (1) | 151224 | 0% | 0 | 0 | 0%
20
21 | Flow to Distribution | 109074949.4499 | 0% | 0 | 0 | 0%
22
23 | Distribution Substation Losses | -460540.3532 | 0.4222% | 1.0042 | 0 | 0%
24
25 | Flow to Primary Lines | 108614409.0967 | 0% | 0 | 0 | 0%
26
27 | Primary Line Losses | -568396.5565 | 0.5233% | 1.0053 | 0 | 0%
28
29 | Flow on Primary | 108046012.5402 | 0% | 0 | 0 | 0%
30
31 | Delivered Sales at Primary | -2479984.651 | 0% | 0 | 1.0267 | 2.6%
32
33 | Flow to Secondary | 105566027.8891 | 0% | 0 | 0 | 0%
34
35 | Transformer Losses | -1916029.7285 | 1.815% | 1.0185 | 0 | 0%
36
37 | Flow on Secondary | 103649998.1607 | 0% | 0 | 0 | 0%
38
39 | Secondary Line & Service Losses | -308309.9067 | 0.2975% | 1.003 | 0 | 0%
40
41 | Balance For Use | 103341688.254 | 0% | 0 | 0 | 0%
42
43 | Company Use | -131587.2357 | 0% | 0 | 0 | 0%
44
45 | Delivered Sales at Secondary | -103210101.0183 | 0% | 0 | 1.0488 | 4.653%
46
47 | NET | 4.4703e-08 | 0% | 0 | 0 | 0%

## LLS_Energy_Losses_by_Rate_Grou
OPC 012981
FPL RC-16
Line No. | Rate Class | Voltage Level (Note 1) | Delivered MWH Sales | Expansion Factor | Delivered Energy at Generation | Delivered Efficiency | Losses | Cost Recovery Multiplier
1
2 | Rate Class Group - | 0 | 0 | 0 | 0 | 0 | 0 | 0
3
4 | CILC-1D / CILC-1G | 0 | 2797965.7976 | 1.0406 | 2911684.7508 | 0.96094 | 113718.9531 | 0.99487
5
6 | GSD-1 / CILC-1G | 0 | 25931180.7767 | 1.0487 | 27194856.0394 | 0.95353 | 1263675.2627 | 1.0026
7
8 | GSLD-2 / OS-2 / MET | 0 | 2604359.1786 | 1.0407 | 2710287.2768 | 0.96092 | 105928.0982 | 0.9949
9
10 | GSLD-3 / CILC-1T | 0 | 1648968.9471 | 1.017 | 1677022.7224 | 0.98327 | 28053.7753 | 0.97228
11
12 | OL-1 / SL-1 | 0 | 649878.1471 | 1.0488 | 681590.1546 | 0.95347 | 31712.0075 | 1.0027
13
14 | SL-2 / GSCU-1 | 0 | 101472.3488 | 1.0488 | 106423.8799 | 0.95347 | 4951.5311 | 1.0027