## Capex & CPVRR Walk from MAP
ESTIMATED CAPEX and CPVRR WALK ($MM)
OPC 002156 FPL RC-16 | MAP 2/4/15 | Module Decision 3/20/15 | Current CAPEX 7/10/15 | Current Var Over/ (Under) MAP | Variance Explanation: Current to MAP
CAPEX (3 Project Portfolio)
DC/AC Ratio |  |  | 1.5
# of Inverters |  |  | 41
°Azimuth |  |  | 195
Net Capacity Factor (NCF) | 26.06% | 26.06% | 26.33% | 0.2668% | Adjust to reflect Hanwha .pan files.
Fixed Capacity Value (FCV) | 52.4% | 52.4% | 53.5% | 1.097% | Increase in NCF with Hanwha .pan files. | September View
BOS | 175.8004 | 168.8719 | 166.9717 | -8.8287 | Adjusted to reflect July 2015 estimated EPC pricing. (1)
Modules | 191.094 | 196.458 | 196.458 | 5.364 | Adjust module price from $0.57 to $0.586/wdc. | Modules | 196.458
Total E&C | 366.8944 | 365.3299 | 363.4297 | -3.4647 |  | Total E&C | 363.4297
Transmission | 25.5 | 25.5 | 6.868 | -18.632 | Based on final (July 2015) T&S budget. | Transmission | 6.868
Development/Ops | 8.9891 | 8.9891 | 7.291 | -1.6981 | Based on July 2015 refresh of Devl/Ops budgets. | Development/Ops | 7.291
Contingency | 8.739 | 8.739 | 7.002 | -1.737 | Reduced base upon which 5% contingency applied. | Contingency | 9.3
SUBTOTAL | 410.1225 | 408.558 | 384.5907 | -25.5318 |  | SUBTOTAL | 386.9
AFUDC | 0 | 9.715 | 9.145 | 9.145 | Need to confirm with FNG. (2) | AFUDC | 11.5
GRAND TOTAL CAPEX | 410.1225 | 418.273 | 393.7358 | -16.3867 |  | GRAND TOTAL CAPEX | 398.4
TOTAL CAPEX ($/kWac) | 1835 | 1871.4674 | 1761.6813 |  |  | TOTAL CAPEX ($/kWac) | 1782.5503
TOTAL CAPEX ($/wdc) | 1.2233 | 1.2476 | 1.1745 |  |  | TOTAL CAPEX ($/wdc) | 1.1884
CPVRR Walk from MAP (3 Project Portfolio) | [5 empty] | CPVRR Walk from MAP (3 Project Portfolio)
Starting Point CPVRR (Estimated) | 0 | 0 | 0 |  |  | Starting Point CPVRR (Estimated) | 0
Adjust Base Capex |  | -1.6925 | -27.6208 |  |  | Adjust Base Capex | -25.1225
Adjust AFUDC |  | 10.5098 | 9.8933 |  | CPVRR estimated based on below sensitivities. | Adjust AFUDC | 12.4409
Adjust O&M Budget |  | -3.4804 | -6.7042 |  |  | Adjust O&M Budget | -6.7042
Adjust Property Tax Abatements |  |  | -2.1 |  | Based on 7/17/15 Executive presentation deck. | Adjust Property Tax Abatements | -2.1
Adjust NCF |  |  | -3.121 |  | CPVRR estimated based on below sensitivities. | Adjust NCF | -3.121
Adjust FCV |  |  | -1.3571 |  | CPVRR estimated based on below sensitivities. | Adjust FCV | -1.3571
REVISED CPVRR: Estimated | 0 | 5.3369 | -31.0098 |  | MAP CPVRR did not include AFUDC. | REVISED CPVRR: Estimated | -25.964
$/wdc Summary (3 Project Portfolio)
BOS (Including Contingency) | 0.55045 | 0.52979 | 0.51894
Modules | 0.57 | 0.586 | 0.586
SUBTOTAL E&C | 1.1205 | 1.1158 | 1.1049
Transmission | 0.076063 | 0.076063 | 0.020486
Development/Ops | 0.026813 | 0.026813 | 0.021748
SUBTOTAL Direct Capex | 1.2233 | 1.2187 | 1.1472
AFUDC | 0 | 0.028978 | 0.027278
GRAND TOTAL | 1.2233 | 1.2476 | 1.1745
(1) MAP capex estimates included a $0.05/wdc target BOS reduction (~ $16.8M for the 3 pack) yet to be identified.
$0.05/wdc target reduction realized within current E&C capex estimate.
(2) All AFUDC estimates assume module cash outflows occur net 15 days after module delivery.
CPVRR Sensitivities (Per Project)
Per 100 bp Δ in NCF | 3.9
Per 100 bp Δ in FCV | 0.4125
Per $1M Δ in Capex | 1.0818
Per $1/kWyr levelized O&M | 1.0504

## CPVRR Sensitivities
DRAFT | Source: Results - Economics of DeSoto 75 MW AC Installation 1 3 DC-AC South West 195 deg_10-20-14.xlsx attached to 10/20/14 Chad Little E-mail
OPC 002157 FPL RC-16
System Assumptions:
- Load forecast = October 1, 2013
- Turkey Point 6 and 7 in-service 2026 & 2027
- Cedar Bay retired
- No GT replacement
- Putnam retires in 2015
Economics of DeSoto 75 MW AC installation, 1.3 DC/AC SW 195 deg
| Capacity AC- MW | Panel Manufacturer | Orientation | Type | DC/AC ratio | In-service date | FCV (% of nameplate) | Capacity Factor (1st year) | Annual Degradation % | All-in Project Cost $ (dec 2016 i/s d) | $/kWac | O&M Cost $/kW (2014)
| 75 | Sun Ed | South West 195 | Fixed | 1.3 | 2016-12-01 | 45.42% | 23.13% | 0.3% | 136683000 | 1822.44 | 5.5
[9 empty] | Revised # ==> | 134011000
CPVRR $ Millions 2014
| Results from Optimization run | 20.6
| Change degradation to .3% | 18.2 |  | Reflect tax abatement | 12.8
| Reduction in Capital Cost from $137M to $134M | 15.6 |  | 1% increase in capacity factor | 11.7 | (from 23 to 24 %)
|  |  |  | 5% increase in firm capacity value | 14.5 | (from 34 MW to 36 MW)
Sensitivities
$MM CPVRR Δ per $1MM Δ in capex |  |  | 1.0818 |  | FCV @ 34 MW | 45.33%
$MM CPVRR Δ per 100 bp Δ in NCF |  |  | 3.9 |  | FCV @ 36 MW | 48%
$MM CPVRR Δ per 100 bp Δ in Capacity Value |  |  | 0.4125 |  | Delta FCV | 2.667%
Note on D28: Use calculations from Fng Model run as it's unclear whether the above calculations capture ALL the stand alone impacts capex changes have on CPVRR.

## Enjamio 5-13-15 O&M Sensitivity
OPC 002158 FPL RC-16 | SOURCE: ENJAMIO 5/13/15 E-MAIL
If we convert the O&M budget provided by PGD into a starting point (in $/KW) that escalates at 2.5% a year and that yields
the same NPV as the PGD budget we come up with 6.80 $/KW
If we reduce that value by 1 $/KW (to 5.8 $/KW) the CPVRR is reduced by $1.05 million CPVRR
| Provided | escalation=2.5%
| by PGD |  | Levelized to a starting point
| 1-74.5 MW PV | used in the analysis | and escalating at 2.5% a year |  |  | Starting point redeuced
| O&M | 1-74.5 MW PV | 1-74.5 MW PV |  |  | by $1/KW
| Un-escalated | O&M | O&M |  |  | [5.8 $/KW]
| 2016 $ | Nominal | Nominal |  |  | Nominal
| $million | $million | $million |  |  | $million
2015 | 0 | 0 | 0 |  |  | 0
2016 | 0 | 0 | 0 | 2017 value converted | $/KW | 0
2017 | 0.4013 | 0.4013 | 0.50644 | to $/KW | 6.7978 | 0.4321
2018 | 0.45 | 0.46125 | 0.5191 |  | escalating at 2.5% a year | 0.4429
2019 | 0.45 | 0.47278 | 0.53207 |  |  | 0.45398
2020 | 0.45 | 0.4846 | 0.54538 |  |  | 0.46532
2021 | 0.45 | 0.49671 | 0.55901 |  |  | 0.47696
2022 | 0.51895 | 0.58715 | 0.57299 |  |  | 0.48888
2023 | 0.53685 | 0.62258 | 0.58731 |  |  | 0.5011
2024 | 0.56059 | 0.66636 | 0.60199 |  |  | 0.51363
2025 | 0.55742 | 0.67916 | 0.61704 |  |  | 0.52647
2026 | 0.55672 | 0.69527 | 0.63247 |  |  | 0.53963
2027 | 0.5497 | 0.70366 | 0.64828 |  |  | 0.55312
2028 | 0.53951 | 0.70788 | 0.66449 |  |  | 0.56695
2029 | 0.52996 | 0.71273 | 0.6811 |  |  | 0.58113
2030 | 0.52403 | 0.72237 | 0.69813 |  |  | 0.59565
2031 | 0.52283 | 0.73875 | 0.71558 |  |  | 0.61055
2032 | 0.53565 | 0.77579 | 0.73347 |  |  | 0.62581
2033 | 0.53029 | 0.78722 | 0.75181 |  |  | 0.64145
2034 | 0.5402 | 0.82198 | 0.7706 |  |  | 0.65749
2035 | 0.53815 | 0.83932 | 0.78987 |  |  | 0.67393
2036 | 0.53935 | 0.86223 | 0.80961 |  |  | 0.69078
2037 | 0.53878 | 0.88285 | 0.82985 |  |  | 0.70805
2038 | 0.53707 | 0.90206 | 0.8506 |  |  | 0.72575
2039 | 0.53502 | 0.92107 | 0.87186 |  |  | 0.74389
2040 | 0.53328 | 0.94102 | 0.89366 |  |  | 0.76249
2041 | 0.53224 | 0.96268 | 0.916 |  |  | 0.78155
2042 | 0.53198 | 0.98627 | 0.9389 |  |  | 0.80109
2043 | 0.51225 | 0.97342 | 0.96238 |  |  | 0.82112
2044 | 0.49435 | 0.96289 | 0.98644 |  |  | 0.84164
2045 | 0.46412 | 0.9266 | 1.0111 |  |  | 0.86269
2046 | 0.42547 | 0.87068 | 1.0364 |  |  | 0.88425
NPV 2015 |  | 7.1589 | 7.156 |  |  | 6.1056
1.0504

## O&M Reduction Detail
DRAFT |  |  |  | OPC 002159 FPL RC-16
(Attorney-Client Work Product)
SOURCE: ENJAMIO 3/6/15 E-MAIL
Solar O&M: 1-74 MW Project |  |  | CURRENT (7/10/15)
| MAP | @ 3/20/15 | Manatee | OPC 002158 FPL RC-16 |  |  | Previous | Current | Manatee | Citrus & Babcock
[7 empty] | Capital | Capital | 2015-07-10 | 2015-07-10
Year | $ | $ | $ | $ |  | Year | $ | $ | $ | $
2015 | 0 | 0 | 0 | 0 |  | 2015 | 0 | 0 | 0 | 0
2016 | 0 | 0 | 0 | 0 |  | 2016 | 0 | 0 | 0 | 0
2017 | 411331.2569 | 411331.2569 | 291511.2291 | 281004.9791 |  | 2017 | 256352.5 | 256352.5 | 245300 | 245300
2018 | 472776.2658 | 472776.2658 | 342466.9247 | 331698.0185 |  | 2018 | 0 | 0 | 0 | 0
2019 | 484595.6724 | 484595.6724 | 351028.5978 | 339990.4689 |  | 2019 | 0 | 0 | 0 | 0
2020 | 496710.5642 | 441352.8888 | 359804.3128 | 348490.2306 |  | 2020 | 0 | 261382.8925 | 0 | 0
2021 | 509128.3283 | 395645.0938 | 368799.4206 | 357202.4864
2022 | 601824.7584 | 485504.443 | 448613.5948 | 448613.5948 |  |  | 221788.9135 | 403772.7642 | 212226.6039 | 212226.6039
2023 | 638149.3216 | 518920.9983 | 469517.9478 | 469517.9478
2024 | 683024.1025 | 560815.0711 | 484299.2618 | 484299.2618 |  |  | Previous | Current
2025 | 696138.9881 | 597116.4641 | 492528.4614 | 492528.4614 |  | Total for one site | 7559706.7139 | 6632034.6952
2026 | 712649.0767 | 584253.2131 | 495910.3885 | 495910.3885
2027 | 721255.6931 | 589649.9329 | 497794.1033 | 497794.1033 |  | reduction for one site | 927672.0187
2028 | 725577.2865 | 590681.3823 | 501845.6668 | 501845.6668
2029 | 730548.9512 | 621246.6127 | 510551.6197 | 510551.6197 |  | reduction for three sites | 2783016.0561
2030 | 740434.2606 | 598709.2512 | 524381.637 | 524381.637
2031 | 757217.5456 | 611949.411 | 541997.5404 | 541997.5404
2032 | 795182.4148 | 646282.5769 | 561207.1216 | 561207.1216
2033 | 806896.8937 | 686247.5635 | 579997.8429 | 579997.8429
2034 | 842531.3927 | 686093.5005 | 605149.8747 | 605149.8747
2035 | 860307.4521 | 699958.6126 | 612392.01 | 612392.01
2036 | 883790.4829 | 719432.9224 | 626137.4852 | 626137.4852
2037 | 904919.7748 | 771745.4888 | 639233.7399 | 639233.7399
2038 | 924607.6988 | 751929.5367 | 652605.8487 | 652605.8487
2039 | 944097.0996 | 767101.9836 | 666995.6062 | 666995.6062
2040 | 964549.5666 | 783129.5726 | 682791.5591 | 682791.5591
2041 | 986742.8116 | 839743.3182 | 699982.7268 | 699982.7268
2042 | 1010924.4888 | 820320.1076 | 718230.6556 | 718230.6556
2043 | 997755.9223 | 802386.4316 | 707839.2151 | 707839.2151
2044 | 986967.1186 | 786713.3907 | 694982.0387 | 694982.0387
2045 | 949769.5436 | 787509.6078 | 662057.532 | 662057.532
2046 | 892442.0242 | 682050.4512 | 614522.6267 | 614522.6267
$/kW-yr | 3.3054
NPV = | 7310573.7106 | 6205678.3494 | 5209815.545 | 5168455.0759 | with 7.54% DR (DR assumed in 2/4/15 executive presentation deck…MAP)
NPV = | 7337917.8004 | 6228261.931 | 5229201.364 | 5187795.8147 | with 7.51% DR
Delta from MAP |  | -1104895.3612 | -2100758.1656 | -2142118.6347
NPV For 3 Projects |  | -3314686.0836 |  | -6384995.4351
CPVRR Multiplier |  | 1.05 |  | 1.05
CPVRR For 3 Projects |  | -3480420.3878 |  | -6704245.2068

## MAP O&M
OPC 002160 FPL RC-16 | 74 MW SOLAR PV O&M - FIXED TILT |  |  |  |  | Project MW | 74
[6 empty] | Inflation | 2.5%
[6 empty] | WACC | 7.54%
|  | Year | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046
|  | # years | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
DECEMBER 2014 PGD ESTIMATE
| O&M ($) | 2014$ | 381961.9628 | 428311.9628 | 428311.9628 | 428311.9628 | 428311.9628 | 493945.6067 | 510984.2608 | 533577.3372 | 530558.6975 | 529894.415 | 523213.5758 | 513510.7783 | 504418.8884 | 498774.9795 | 497639.6281 | 509843.8561 | 504736.3713 | 514172.4274 | 512215.2585 | 513362.6663 | 512815.537 | 511192.8089 | 509237.0911 | 507579.4725 | 506593.4913 | 506349.6174 | 487564.6585 | 470529.3543 | 441751.8854 | 404963.9091
| O&M ($) | 2016 $ | 401298.7872 | 449995.2559 | 449995.2559 | 449995.2559 | 449995.2559 | 518951.6031 | 536852.839 | 560589.6899 | 557418.2315 | 556720.3197 | 549701.2631 | 539507.2614 | 529955.0946 | 524025.4629 | 522832.6342 | 535654.7013 | 530288.6501 | 540202.4066 | 538146.1559 | 539351.6513 | 538776.8236 | 537071.9449 | 535017.2188 | 533275.6832 | 532239.7868 | 531983.5668 | 512247.6193 | 494349.9029 | 464115.5746 | 425465.207
| O&M ($) | Nominal | 411331.2569 | 472776.2658 | 484595.6724 | 496710.5642 | 509128.3283 | 601824.7584 | 638149.3216 | 683024.1025 | 696138.9881 | 712649.0767 | 721255.6931 | 725577.2865 | 730548.9512 | 740434.2606 | 757217.5456 | 795182.4148 | 806896.8937 | 842531.3927 | 860307.4521 | 883790.4829 | 904919.7748 | 924607.6988 | 944097.0996 | 964549.5666 | 986742.8116 | 1010924.4888 | 997755.9223 | 986967.1186 | 949769.5436 | 892442.0242
| O&M ($/kW) | 2014$ | 5.1616 | 5.788 | 5.788 | 5.788 | 5.788 | 6.6749 | 6.9052 | 7.2105 | 7.1697 | 7.1607 | 7.0705 | 6.9393 | 6.8165 | 6.7402 | 6.7249 | 6.8898 | 6.8208 | 6.9483 | 6.9218 | 6.9373 | 6.9299 | 6.908 | 6.8816 | 6.8592 | 6.8459 | 6.8426 | 6.5887 | 6.3585 | 5.9696 | 5.4725
| O&M ($/kW) | 2016 $ | 5.423 | 6.081 | 6.081 | 6.081 | 6.081 | 7.0129 | 7.2548 | 7.5755 | 7.5327 | 7.5232 | 7.4284 | 7.2906 | 7.1616 | 7.0814 | 7.0653 | 7.2386 | 7.1661 | 7.3 | 7.2722 | 7.2885 | 7.2808 | 7.2577 | 7.23 | 7.2064 | 7.1924 | 7.189 | 6.9223 | 6.6804 | 6.2718 | 5.7495
| O&M ($/kW) | Nominal | 5.5585 | 6.3889 | 6.5486 | 6.7123 | 6.8801 | 8.1328 | 8.6236 | 9.2301 | 9.4073 | 9.6304 | 9.7467 | 9.8051 | 9.8723 | 10.0059 | 10.2327 | 10.7457 | 10.904 | 11.3856 | 11.6258 | 11.9431 | 12.2286 | 12.4947 | 12.7581 | 13.0345 | 13.3344 | 13.6611 | 13.4832 | 13.3374 | 12.8347 | 12.06
| 30 year avgerage O&M ($/kW) | 2014$ | 6.5967
| 30 year avgerage O&M ($/kW) | 2016 $ | 6.9306
| 30 year avgerage O&M ($/kW) | Nominal | 10.4202
| 30 year PV O&M ($ MM) | 2016 $ | 7861790.9684 | --> for one 74 MW site
| 30 year PV O&M ($ MM) | 2016 $ | 23585372.9052 | --> for three 74 MW sites

## 3-20-15 O&M
OPC 002161 FPL RC-16 | 74 MW SOLAR PV O&M - FIXED TILT |  |  |  |  | Project MW | 74
[6 empty] | Inflation | 2.5%
[6 empty] | WACC | 7.54%
|  | Year | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046
|  | # years | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
FEBRUARY 2015 PGD ESTIMATE
| O&M | 2014$ | 381961.9628 | 428311.9628 | 428311.9628 | 380577.2128 | 332842.4628 | 398476.1067 | 415514.7608 | 438107.8372 | 455089.1975 | 434424.915 | 427744.0758 | 418041.2783 | 428949.3884 | 403305.4795 | 402170.1281 | 414374.3561 | 429266.8713 | 418702.9274 | 416745.7585 | 417893.1663 | 437346.037 | 415723.3089 | 413767.5911 | 412109.9725 | 431123.9913 | 410880.1174 | 392095.1585 | 375059.8543 | 366282.3854 | 309494.4091
| O&M ($) | 2016 $ | 401298.7872 | 449995.2559 | 449995.2559 | 399843.9342 | 349692.6125 | 418648.9596 | 436550.1956 | 460287.0465 | 478128.0881 | 456417.6763 | 449398.6197 | 439204.618 | 450664.9512 | 423722.8194 | 422529.9908 | 435352.0579 | 450998.5067 | 439899.7631 | 437843.5125 | 439049.0079 | 459486.6801 | 436769.3015 | 434714.5754 | 432973.0398 | 452949.6434 | 431680.9233 | 411944.9759 | 394047.2595 | 384825.4311 | 325162.5636
| O&M ($) | Nominal | 411331.2569 | 472776.2658 | 484595.6724 | 441352.8888 | 395645.0938 | 485504.443 | 518920.9983 | 560815.0711 | 597116.4641 | 584253.2131 | 589649.9329 | 590681.3823 | 621246.6127 | 598709.2512 | 611949.411 | 646282.5769 | 686247.5635 | 686093.5005 | 699958.6126 | 719432.9224 | 771745.4888 | 751929.5367 | 767101.9836 | 783129.5726 | 839743.3182 | 820320.1076 | 802386.4316 | 786713.3907 | 787509.6078 | 682050.4512
| O&M ($/kW) | 2014$ | 5.1616 | 5.788 | 5.788 | 5.1429 | 4.4979 | 5.3848 | 5.6151 | 5.9204 | 6.1499 | 5.8706 | 5.7803 | 5.6492 | 5.7966 | 5.4501 | 5.4347 | 5.5997 | 5.8009 | 5.6581 | 5.6317 | 5.6472 | 5.9101 | 5.6179 | 5.5915 | 5.5691 | 5.826 | 5.5524 | 5.2986 | 5.0684 | 4.9498 | 4.1824
| O&M ($/kW) | 2016 $ | 5.423 | 6.081 | 6.081 | 5.4033 | 4.7256 | 5.6574 | 5.8993 | 6.2201 | 6.4612 | 6.1678 | 6.073 | 5.9352 | 6.0901 | 5.726 | 5.7099 | 5.8831 | 6.0946 | 5.9446 | 5.9168 | 5.9331 | 6.2093 | 5.9023 | 5.8745 | 5.851 | 6.1209 | 5.8335 | 5.5668 | 5.325 | 5.2003 | 4.3941
| O&M ($/kW) | Nominal | 5.5585 | 6.3889 | 6.5486 | 5.9642 | 5.3466 | 6.5609 | 7.0124 | 7.5786 | 8.0691 | 7.8953 | 7.9682 | 7.9822 | 8.3952 | 8.0907 | 8.2696 | 8.7335 | 9.2736 | 9.2715 | 9.4589 | 9.7221 | 10.429 | 10.1612 | 10.3662 | 10.5828 | 11.3479 | 11.0854 | 10.8431 | 10.6313 | 10.642 | 9.2169
| 30 year avgerage O&M ($/kW) | 2014$ | 5.5111
| 30 year avgerage O&M ($/kW) | 2016 $ | 5.7901
| 30 year avgerage O&M ($/kW) | Nominal | 8.6465
| 30 year PV O&M ($ MM) | 2016 $ | 6673586.497 | --> for one 74 MW site
| 30 year PV O&M ($ MM) | 2016 $ | 20020759.4909 | --> for three 74 MW sites

## 7-10-15 O&M
MANATEE MW SOLAR PV O&M - FIXED TILT | Project MW | 74 |  | Inputs in red font
OPC 002162 FPL RC-16 | Inflation | 2.5%
| WACC | 7.51%
| Year | COD Dec 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046
| # years | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | TOTAL
O&M
O&M ($) | 2015 |  | 277464.5845 | 318014.5845 | 318014.5845 | 318014.5845 | 318014.5845 | 377403.0213 | 385355.2456 | 387792.1545 | 384762.4469 | 377955.515 | 370137.735 | 364049.0722 | 361331.2661 | 362067.459 | 365103.0571 | 368822.5463 | 371874.8444 | 378538.0192 | 373725.0494 | 372793.6717 | 371308.2947 | 369829.932 | 368765.432 | 368291.3415 | 368355.2153 | 368739.4234 | 354540.9372 | 339610.7934 | 315631.0855 | 285823.5777 | 10662130.059
O&M ($) | 2016 |  | 284401.1992 | 325964.9492 | 325964.9492 | 325964.9492 | 325964.9492 | 386838.0968 | 394989.1268 | 397486.9584 | 394381.508 | 387404.4029 | 379391.1784 | 373150.299 | 370364.5478 | 371119.1454 | 374230.6335 | 378043.1099 | 381171.7155 | 388001.4697 | 383068.1756 | 382113.5134 | 380591.0021 | 379075.6803 | 377984.5678 | 377498.6251 | 377564.0956 | 377957.909 | 363404.4606 | 348101.0632 | 323521.8627 | 292969.1671
O&M ($) | Nominal |  | 291511.2291 | 342466.9247 | 351028.5978 | 359804.3128 | 368799.4206 | 448613.5948 | 469517.9478 | 484299.2618 | 492528.4614 | 495910.3885 | 497794.1033 | 501845.6668 | 510551.6197 | 524381.637 | 541997.5404 | 561207.1216 | 579997.8429 | 605149.8747 | 612392.01 | 626137.4852 | 639233.7399 | 652605.8487 | 666995.6062 | 682791.5591 | 699982.7268 | 718230.6556 | 707839.2151 | 694982.0387 | 662057.532 | 614522.6267
O&M ($/kW) | 2015 |  | 3.7495 | 4.2975 | 4.2975 | 4.2975 | 4.2975 | 5.1 | 5.2075 | 5.2404 | 5.1995 | 5.1075 | 5.0019 | 4.9196 | 4.8829 | 4.8928 | 4.9338 | 4.9841 | 5.0253 | 5.1154 | 5.0503 | 5.0378 | 5.0177 | 4.9977 | 4.9833 | 4.9769 | 4.9778 | 4.983 | 4.7911 | 4.5893 | 4.2653 | 3.8625
O&M ($/kW) | 2016 |  | 3.8433 | 4.4049 | 4.4049 | 4.4049 | 4.4049 | 5.2275 | 5.3377 | 5.3714 | 5.3295 | 5.2352 | 5.1269 | 5.0426 | 5.0049 | 5.0151 | 5.0572 | 5.1087 | 5.151 | 5.2433 | 5.1766 | 5.1637 | 5.1431 | 5.1226 | 5.1079 | 5.1013 | 5.1022 | 5.1075 | 4.9109 | 4.7041 | 4.3719 | 3.959
O&M ($/kW) | Nominal |  | 3.9393 | 4.6279 | 4.7436 | 4.8622 | 4.9838 | 6.0623 | 6.3448 | 6.5446 | 6.6558 | 6.7015 | 6.7269 | 6.7817 | 6.8993 | 7.0862 | 7.3243 | 7.5839 | 7.8378 | 8.1777 | 8.2756 | 8.4613 | 8.6383 | 8.819 | 9.0135 | 9.2269 | 9.4592 | 9.7058 | 9.5654 | 9.3916 | 8.9467 | 8.3044
30 year average O&M ($/kW) | 2015 |  | 2017: 4.8028
30 year average O&M ($/kW) | 2016 |  | 2017: 4.9228
30 year average O&M ($/kW) | Nominal |  | 2017: 7.3897
30 year PV O&M ($ MM) | 2016 |  | 2017: 5.6219
CapEx
CapEx ($) | 2016 | 245300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CapEx ($) | 2016 | 245300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CapEx ($) | Nominal | 245300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11696.6678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14251.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CapEx ($/kW) | 2016 | 3.3149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CapEx ($/kW) | 2016 | 3.3149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CapEx ($/kW) | Nominal | 3.3149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 year average CapEx ($/kW) | 2016 |  | 2017: 0.0086486
30 year average CapEx ($/kW) | 2016 |  | 2017: 0.0086486
30 year average CapEx ($/kW) | Nominal |  | 2017: 0.011688
30 year PV CapEx ($ MM) | 2016 | 0.25633
|  |  | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046
|  |  | 536811.2291 | 342466.9247 | 351028.5978 | 359804.3128 | 368799.4206 | 448613.5948 | 469517.9478 | 495995.9296 | 492528.4614 | 495910.3885 | 497794.1033 | 501845.6668 | 510551.6197 | 524381.637 | 541997.5404 | 575458.3755 | 579997.8429 | 605149.8747 | 612392.01 | 626137.4852 | 639233.7399 | 652605.8487 | 666995.6062 | 682791.5591 | 699982.7268 | 718230.6556 | 707839.2151 | 694982.0387 | 662057.532 | 614522.6267
| FC SS Inputs: | (M$) | 0.53681 | 0.34247 | 0.35103 | 0.3598 | 0.3688 | 0.44861 | 0.46952 | 0.496 | 0.49253 | 0.49591 | 0.49779 | 0.50185 | 0.51055 | 0.52438 | 0.542 | 0.57546 | 0.58 | 0.60515 | 0.61239 | 0.62614 | 0.63923 | 0.65261 | 0.667 | 0.68279 | 0.69998 | 0.71823 | 0.70784 | 0.69498 | 0.66206 | 0.61452
CITRUS & BABCOCK 74 MW SOLAR PV O&M - FIXED TILT | Project MW | 74 | 2018: Inputs in red font
| Inflation | 2.5%
| WACC | 7.51%
| Year | COD Dec 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046
| # years | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | TOTAL
O&M
O&M ($) | 2015 |  | 267464.5845 | 308014.5845 | 308014.5845 | 308014.5845 | 308014.5845 | 377403.0213 | 385355.2456 | 387792.1545 | 384762.4469 | 377955.515 | 370137.735 | 364049.0722 | 361331.2661 | 362067.459 | 365103.0571 | 368822.5463 | 371874.8444 | 378538.0192 | 373725.0494 | 372793.6717 | 371308.2947 | 369829.932 | 368765.432 | 368291.3415 | 368355.2153 | 368739.4234 | 354540.9372 | 339610.7934 | 315631.0855 | 285823.5777 | 10612130.059
O&M ($) | 2016 |  | 274151.1992 | 315714.9492 | 315714.9492 | 315714.9492 | 315714.9492 | 386838.0968 | 394989.1268 | 397486.9584 | 394381.508 | 387404.4029 | 379391.1784 | 373150.299 | 370364.5478 | 371119.1454 | 374230.6335 | 378043.1099 | 381171.7155 | 388001.4697 | 383068.1756 | 382113.5134 | 380591.0021 | 379075.6803 | 377984.5678 | 377498.6251 | 377564.0956 | 377957.909 | 363404.4606 | 348101.0632 | 323521.8627 | 292969.1671
O&M ($) | Nominal |  | 281004.9791 | 331698.0185 | 339990.4689 | 348490.2306 | 357202.4864 | 448613.5948 | 469517.9478 | 484299.2618 | 492528.4614 | 495910.3885 | 497794.1033 | 501845.6668 | 510551.6197 | 524381.637 | 541997.5404 | 561207.1216 | 579997.8429 | 605149.8747 | 612392.01 | 626137.4852 | 639233.7399 | 652605.8487 | 666995.6062 | 682791.5591 | 699982.7268 | 718230.6556 | 707839.2151 | 694982.0387 | 662057.532 | 614522.6267
O&M ($/kW) | 2015 |  | 3.6144 | 4.1624 | 4.1624 | 4.1624 | 4.1624 | 5.1 | 5.2075 | 5.2404 | 5.1995 | 5.1075 | 5.0019 | 4.9196 | 4.8829 | 4.8928 | 4.9338 | 4.9841 | 5.0253 | 5.1154 | 5.0503 | 5.0378 | 5.0177 | 4.9977 | 4.9833 | 4.9769 | 4.9778 | 4.983 | 4.7911 | 4.5893 | 4.2653 | 3.8625
O&M ($/kW) | 2016 |  | 3.7047 | 4.2664 | 4.2664 | 4.2664 | 4.2664 | 5.2275 | 5.3377 | 5.3714 | 5.3295 | 5.2352 | 5.1269 | 5.0426 | 5.0049 | 5.0151 | 5.0572 | 5.1087 | 5.151 | 5.2433 | 5.1766 | 5.1637 | 5.1431 | 5.1226 | 5.1079 | 5.1013 | 5.1022 | 5.1075 | 4.9109 | 4.7041 | 4.3719 | 3.959
O&M ($/kW) | Nominal |  | 3.7974 | 4.4824 | 4.5945 | 4.7093 | 4.8271 | 6.0623 | 6.3448 | 6.5446 | 6.6558 | 6.7015 | 6.7269 | 6.7817 | 6.8993 | 7.0862 | 7.3243 | 7.5839 | 7.8378 | 8.1777 | 8.2756 | 8.4613 | 8.6383 | 8.819 | 9.0135 | 9.2269 | 9.4592 | 9.7058 | 9.5654 | 9.3916 | 8.9467 | 8.3044
30 year average O&M ($/kW) | 2015 |  | 2017: 4.7802
30 year average O&M ($/kW) | 2016 |  | 2017: 4.8997
30 year average O&M ($/kW) | Nominal |  | 2017: 7.3648
30 year PV O&M ($ MM) | 2016 |  | 2017: 5.5774
CapEx
CapEx ($) | 2016 | 245300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CapEx ($) | 2016 | 245300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CapEx ($) | Nominal | 245300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11696.6678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14251.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CapEx ($/kW) | 2016 | 3.3149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CapEx ($/kW) | 2016 | 3.3149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CapEx ($/kW) | Nominal | 3.3149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 year average CapEx ($/kW) | 2016 |  | 2017: 0.0086486
30 year average CapEx ($/kW) | 2016 |  | 2017: 0.0086486
30 year average CapEx ($/kW) | Nominal |  | 2017: 0.011688
30 year PV CapEx ($ MM) | 2016 | 0.25633
|  |  | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046
|  |  | 526304.9791 | 331698.0185 | 339990.4689 | 348490.2306 | 357202.4864 | 448613.5948 | 469517.9478 | 495995.9296 | 492528.4614 | 495910.3885 | 497794.1033 | 501845.6668 | 510551.6197 | 524381.637 | 541997.5404 | 575458.3755 | 579997.8429 | 605149.8747 | 612392.01 | 626137.4852 | 639233.7399 | 652605.8487 | 666995.6062 | 682791.5591 | 699982.7268 | 718230.6556 | 707839.2151 | 694982.0387 | 662057.532 | 614522.6267
| FC SS Inputs: | (M$) | 0.5263 | 0.3317 | 0.33999 | 0.34849 | 0.3572 | 0.44861 | 0.46952 | 0.496 | 0.49253 | 0.49591 | 0.49779 | 0.50185 | 0.51055 | 0.52438 | 0.542 | 0.57546 | 0.58 | 0.60515 | 0.61239 | 0.62614 | 0.63923 | 0.65261 | 0.667 | 0.68279 | 0.69998 | 0.71823 | 0.70784 | 0.69498 | 0.66206 | 0.61452

## MAP NCF & FCV Detail
SOURCE: ECCLESTON 7/14/15 E-MAIL |  |  |  | OPC 002163 FPL RC-16
FPLC - DeSoto, Florida
Lat: N 27.3 ; Lon: W 81.8 (WGS84)
Axis Tilt | F20 | degrees
Azimuth | 195 | degrees
AC Size | 75 | MW
DC to AC Ratio | 1.5
Degraded
Net Capacity Factor - SunEdison 345W - F20 - SMA 750CP-US | Column Labels | [13 empty] | Month 8
Row Labels | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | Grand Total |  | Hour 17
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1.5003e-05 | 0.019227 | 0 | 0.019505 | 0.062725 | 0.066083 | 0.053355 | 0.02062 | 0.00037661 | 0 | 0.083498 | 0.0043174 | 0.027382
9 | 0.2385 | 0.2618 | 0.10294 | 0.18688 | 0.22785 | 0.20886 | 0.18996 | 0.16967 | 0.15174 | 0.14028 | 0.36966 | 0.26842 | 0.20907
10 | 0.51108 | 0.52169 | 0.37743 | 0.47895 | 0.48923 | 0.43508 | 0.43095 | 0.41869 | 0.4055 | 0.41614 | 0.60285 | 0.50426 | 0.46537
11 | 0.7135 | 0.72593 | 0.63661 | 0.71898 | 0.70392 | 0.63468 | 0.64098 | 0.63608 | 0.62194 | 0.65054 | 0.76916 | 0.6845 | 0.67759
12 | 0.80439 | 0.79577 | 0.80826 | 0.87154 | 0.85336 | 0.76505 | 0.76273 | 0.77549 | 0.76407 | 0.80171 | 0.82074 | 0.76124 | 0.79865
13 | 0.79615 | 0.79248 | 0.83315 | 0.89629 | 0.88396 | 0.80848 | 0.8231 | 0.841 | 0.79793 | 0.82788 | 0.82161 | 0.76531 | 0.82413
14 | 0.79539 | 0.76576 | 0.84068 | 0.88554 | 0.88502 | 0.79598 | 0.82068 | 0.80005 | 0.7891 | 0.81189 | 0.79096 | 0.74876 | 0.81114
15 | 0.74493 | 0.73425 | 0.83407 | 0.87724 | 0.85074 | 0.75008 | 0.79788 | 0.7746 | 0.76685 | 0.79762 | 0.68915 | 0.66172 | 0.77361
16 | 0.62247 | 0.65983 | 0.79999 | 0.84893 | 0.80254 | 0.68782 | 0.69431 | 0.68962 | 0.67631 | 0.72237 | 0.54711 | 0.54 | 0.69121
17 | 0.41064 | 0.46955 | 0.7204 | 0.75422 | 0.67696 | 0.54037 | 0.54333 | 0.54484 | 0.52208 | 0.5663 | 0.29356 | 0.28337 | 0.5276 | FCV ==> | 0.52403
18 | 0.07937 | 0.19055 | 0.52907 | 0.53571 | 0.48217 | 0.3833 | 0.37567 | 0.34865 | 0.34469 | 0.32939 | 0.0022707 | 0.0033917 | 0.30108
19 | 0 | 0 | 0.26108 | 0.26747 | 0.25717 | 0.19864 | 0.19582 | 0.17788 | 0.13308 | 0.059394 | 0 | 0 | 0.13005
20 | 0 | 0 | 0.0021163 | 0.02623 | 0.049436 | 0.055429 | 0.058642 | 0.030077 | 0.00063537 | 0 | 0 | 0 | 0.018677
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grand Total | 0.23819 | 0.24737 | 0.28107 | 0.30698 | 0.30104 | 0.26374 | 0.26614 | 0.25947 | 0.24893 | 0.25515 | 0.24127 | 0.21772 | 0.26065
Name | Loss (%)
Transposition on POA | 8.27
Shading | -1.77
IAM Factor | -2.38
Temperature | -8.84
Irradiance | -0.36
Soiling | -1.01
Module Quality | -2.52
Module Mismatch | -1.01
DC Wiring | -0.97
Inverter Efficiency | -1.87
Inverter Clipping | -2.59
Inverter Voltage | 0
AC Wiring | -0.3
MV Transformer | -0.9
HV Transformer | -0.55
Note on P27: Author: Per Miller 6/4/15, only degrade through 2030 as that is the last year we have non generic (Nuclear) generation in our plan. Post 2030, the next unit is a generic unit which would be affected by solar firm capacity.

## 7-10-15 NCF & FCV
Source: Applicable Excel file attached to Kristen Bradford 6/1/15 e-mail. | [7 empty] | OPC 002164 FPL RC-16
FPLC - Citrus, FL
Lat: N 27.3 ; Lon: W 81.8 (WGS84)
Axis Tilt | F20 | degrees
Azimuth | 195 | degrees
AC Size | 74.5 | MW
DC to AC Ratio | 1.5
Degraded
Net Capacity Factor - Hanwha 325W - F20 - GE ProSolar 2MW | [14 empty] | Month 8
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | Grand Total |  | Hour 17
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1.03e-05 | 0.018866 | 0 | 0.01895 | 0.062834 | 0.06642 | 0.053179 | 0.019764 | 0.000313 | 0 | 0.083914 | 0.004031 | 0.027262
9 | 0.24274 | 0.26641 | 0.10396 | 0.18947 | 0.23215 | 0.21285 | 0.19324 | 0.17245 | 0.15424 | 0.14242 | 0.37471 | 0.27297 | 0.21248
10 | 0.51333 | 0.52449 | 0.38313 | 0.48496 | 0.49605 | 0.44216 | 0.43837 | 0.42589 | 0.4119 | 0.42186 | 0.60686 | 0.50674 | 0.47071
11 | 0.71971 | 0.73469 | 0.64101 | 0.72626 | 0.71294 | 0.64321 | 0.64925 | 0.64458 | 0.6303 | 0.65779 | 0.78063 | 0.69176 | 0.68551
12 | 0.80859 | 0.79927 | 0.81553 | 0.87721 | 0.86689 | 0.77995 | 0.77768 | 0.79048 | 0.77786 | 0.81415 | 0.82509 | 0.76681 | 0.80829
13 | 0.79939 | 0.79536 | 0.8363 | 0.89911 | 0.88778 | 0.81472 | 0.83041 | 0.84678 | 0.80383 | 0.83251 | 0.82549 | 0.76945 | 0.82862
14 | 0.7989 | 0.76902 | 0.84346 | 0.88815 | 0.88854 | 0.80125 | 0.82603 | 0.8049 | 0.79439 | 0.81621 | 0.79662 | 0.754 | 0.81545
15 | 0.7522 | 0.73846 | 0.83677 | 0.87979 | 0.85474 | 0.75582 | 0.80368 | 0.7795 | 0.77273 | 0.80271 | 0.70083 | 0.67205 | 0.77946
16 | 0.62874 | 0.66962 | 0.80351 | 0.85309 | 0.80942 | 0.69946 | 0.7043 | 0.69818 | 0.68662 | 0.73467 | 0.55242 | 0.54442 | 0.69895
17 | 0.41428 | 0.47292 | 0.73286 | 0.76838 | 0.6905 | 0.55141 | 0.55467 | 0.55624 | 0.53241 | 0.57447 | 0.29837 | 0.28748 | 0.53667 | FCV ==> | 0.535
18 | 0.080212 | 0.19441 | 0.53357 | 0.54124 | 0.48839 | 0.38894 | 0.38129 | 0.35394 | 0.34968 | 0.33437 | 0.001903 | 0.003024 | 0.30497
19 | 0 | 0 | 0.26644 | 0.2733 | 0.26312 | 0.20288 | 0.19984 | 0.18156 | 0.13576 | 0.05959 | 0 | 0 | 0.13273
20 | 0 | 0 | 0.001684 | 0.025024 | 0.049302 | 0.05542 | 0.058708 | 0.029198 | 0.000489 | 0 | 0 | 0 | 0.018448
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grand Total | 0.23992 | 0.24931 | 0.28326 | 0.30937 | 0.30428 | 0.26727 | 0.26961 | 0.26264 | 0.25211 | 0.25795 | 0.24362 | 0.2197 | 0.26332
Name | Loss (%)
Transposition on POA | 8.27
Shading | -1.77
IAM Factor | -2.01
Soiling | -1
Temperature | -7.62
Irradiance | 0.29
Module Quality | -2
Module Mismatch | -1.5
DC Wiring | -1.03
Inverter Efficiency | -2.12
Inverter Clipping | -2.99
Inverter Voltage | 0
AC Wiring | -0.3
MV Transformer | -0.9
HV Transformer | -0.55
Note on P28: Author: Per Miller 6/4/15, only degrade through 2030 as that is the last year we have non generic (Nuclear) generation in our plan. Post 2030, the next unit is a generic unit which would be affected by solar firm capacity.

## AFUDC SWAG Calcs
INPUTS
Monthly rate post 1/1/04 ==> | not used
Monthly rate pre 1/1/04 ==> | not used
Blended Rate for Budget purposes ==> | not used
Date Capital ER established (MM/DD/YY) ==> | 2015-02-01 | ==> Enter trigger date as 1st day of month
Date Commercial Ops declared (MM/DD/YY) ==> | 2016-10-01 | ==> Enter trigger date as 1st day of month
AFUDC Annual Rate ==> | 6.34% | ==> Per FPL EDM Model
OPC 002165 FPL RC-16 |  |  |  | Monthly AFUDC Rate Applied ==> | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358 | 0.0051358
[5 empty] | 2015 | 2015 | 2015 | 2015 | 2015 | 2015 | 2015 | 2015 | 2015 | 2015 | 2015 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2018 | 2018 | 2018 | 2018 | 2018 | 2018 | 2018 | 2018 | 2018 | 2018 | 2018 | 2018 | 2019 | 2019 | 2019 | 2019 | 2019 | 2019 | 2019
 | time axis 2015-02-01 to 2019-07-31
TOTAL
Calculated AFUDC |  |  | CAPEX
Monthly Expenditures Totals: Accrual Based (excludes demolition) |  |  | 416340000 |  | 3920000 | 780000 | 780000 | 780000 | 780000 | 1890000 | 780000 | 1380000 | 1380000 | 1530000 | 14310000 | 51450000 | 55110000 | 53430000 | 50970000 | 48960000 | 44700000 | 41640000 | 37180000 | 4590000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monthly Expenditures Totals: Cash Based |  |  |  |  | 0 | 3920000 | 780000 | 780000 | 780000 | 780000 | 1890000 | 780000 | 1380000 | 1380000 | 1530000 | 14310000 | 51450000 | 55110000 | 53430000 | 50970000 | 48960000 | 44700000 | 41640000 | 37180000 | 4590000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Expenditure Balance at End of Month |  |  |  |  | 0 | 3920000 | 4700000 | 5480000 | 6260000 | 7040000 | 8930000 | 9710000 | 11090000 | 12470000 | 14000000 | 28310000 | 79760000 | 134870000 | 188300000 | 239270000 | 288230000 | 332930000 | 374570000 | 411750000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000
Average Plant in Service (Beg. + End)/2 |  |  |  |  | 0 | 1960000 | 4310000 | 5090000 | 5870000 | 6650000 | 7985000 | 9320000 | 10400000 | 11780000 | 13235000 | 21155000 | 54035000 | 107315000 | 161585000 | 213785000 | 263750000 | 310580000 | 353750000 | 393160000 | 414045000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000 | 416340000
Applied AFUDC For the Month |  |  |  |  | 0 | 10066.0762 | 22135.0962 | 26140.9837 | 30146.8711 | 34152.7586 | 41008.9891 | 47865.2196 | 53411.833 | 60499.1724 | 67971.6933 | 108646.8584 | 277510.4228 | 551143.3519 | 829860.6766 | 1097946.9923 | 1354554.8997 | 1595062.2208 | 1816772.6853 | 2019172.7179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Applied AFUDC on Prior Month cumulative Balance |  |  |  |  | 0 | 0 | 51.6969 | 165.6428 | 300.7471 | 457.1186 | 634.8664 | 848.7389 | 1098.9218 | 1378.8756 | 1696.6659 | 2054.4654 | 2623.0001 | 4061.6962 | 6913.0923 | 11210.5559 | 16906.9153 | 23950.4046 | 32265.2539 | 41761.4563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total AFUDC for Month |  |  |  |  | 0 | 10066.0762 | 22186.7931 | 26306.6264 | 30447.6182 | 34609.8772 | 41643.8554 | 48713.9585 | 54510.7548 | 61878.048 | 69668.3592 | 110701.3238 | 280133.4229 | 555205.0481 | 836773.769 | 1109157.5482 | 1371461.8149 | 1619012.6254 | 1849037.9392 | 2060934.1742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative AFUDC |  |  |  |  | 0 | 10066.0762 | 32252.8693 | 58559.4957 | 89007.114 | 123616.9911 | 165260.8466 | 213974.8051 | 268485.5599 | 330363.6078 | 400031.967 | 510733.2909 | 790866.7138 | 1346071.7619 | 2182845.5308 | 3292003.079 | 4663464.8939 | 6282477.5194 | 8131515.4586 | 10192449.6328 | 10192449.6328 | 10192449.6328 | 10192449.6328 |  | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987 | 16973296.9987
|  |  | Cumulative AFUDC Calc ==> | 10192449.6328
|  |  | AFUDC Per Simmons | Total AFUDC Calc'd
30% module/30% Inverter downpymnt |  | (1) | 13.7 | 14938408.9714 | 2015-02-01: 3920000; 2015-03-31: 780000; 2015-04-30: 68580000; 2015-05-31: 780000; 2015-06-30: 780000; 2015-07-31: 1890000; 2015-08-31: 780000; 2015-09-30: 1380000; 2015-10-31: 1380000; 2015-11-30: 1530000; 2015-12-31: 14310000; 2016-01-31: 44250000; 2016-02-29: 47880000; 2016-03-31: 46200000; 2016-04-30: 43770000; 2016-05-31: 41730000; 2016-06-30: 37470000; 2016-07-31: 31080000; 2016-08-31: 26590000; 2016-09-30: 1230000
50% module/10% Inverter downpymnt |  | (2) | 15.3 | 16973296.9987 | 2015-02-01: 3920000; 2015-03-31: 780000; 2015-04-30: 100320000; 2015-05-31: 780000; 2015-06-30: 780000; 2015-07-31: 1890000; 2015-08-31: 780000; 2015-09-30: 1380000; 2015-10-31: 1380000; 2015-11-30: 1530000; 2015-12-31: 14310000; 2016-01-31: 39420000; 2016-02-29: 43080000; 2016-03-31: 41400000; 2016-04-30: 38970000; 2016-05-31: 36930000; 2016-06-30: 32670000; 2016-07-31: 29610000; 2016-08-31: 25150000; 2016-09-30: 1230000
0% module/0% Inverter downpymnt (NEER pays downpymnt) |  | (4) | 9.9 | 10192449.6328 | 2015-02-01: 3920000; 2015-03-31: 780000; 2015-04-30: 780000; 2015-05-31: 780000; 2015-06-30: 780000; 2015-07-31: 1890000; 2015-08-31: 780000; 2015-09-30: 1380000; 2015-10-31: 1380000; 2015-11-30: 1530000; 2015-12-31: 14310000; 2016-01-31: 51450000; 2016-02-29: 55110000; 2016-03-31: 53430000; 2016-04-30: 50970000; 2016-05-31: 48960000; 2016-06-30: 44700000; 2016-07-31: 41640000; 2016-08-31: 37180000; 2016-09-30: 4590000
10% module/10% Inverter downpymnt (First Solar) |  | (3) | 11.4 | 12007759.1517 | 2015-02-01: 3920000; 2015-03-31: 780000; 2015-04-30: 24180000; 2015-05-31: 780000; 2015-06-30: 780000; 2015-07-31: 1890000; 2015-08-31: 780000; 2015-09-30: 1380000; 2015-10-31: 1380000; 2015-11-30: 1530000; 2015-12-31: 14310000; 2016-01-31: 49950000; 2016-02-29: 53610000; 2016-03-31: 51930000; 2016-04-30: 49500000; 2016-05-31: 47460000; 2016-06-30: 43200000; 2016-07-31: 40140000; 2016-08-31: 35680000; 2016-09-30: 1230000
30% module/10% Inverter downpymnt (First Solar) |  | (4) | 13.1266 | 14313191.3975 | 2015-02-01: 3920000; 2015-03-31: 780000; 2015-04-30: 59130000; 2015-05-31: 780000; 2015-06-30: 780000; 2015-07-31: 1890000; 2015-08-31: 780000; 2015-09-30: 1380000; 2015-10-31: 1380000; 2015-11-30: 1530000; 2015-12-31: 15450000; 2016-01-31: 45240000; 2016-02-29: 48900000; 2016-03-31: 47220000; 2016-04-30: 44760000; 2016-05-31: 42750000; 2016-06-30: 38490000; 2016-07-31: 31110000; 2016-08-31: 26650000; 2016-09-30: 1230000
|  |  |  | Monthly % Per Above ==> | 2015-02-01: 0.9415%; 2015-03-31: 0.1873%; 2015-04-30: 0.1873%; 2015-05-31: 0.1873%; 2015-06-30: 0.1873%; 2015-07-31: 0.454%; 2015-08-31: 0.1873%; 2015-09-30: 0.3315%; 2015-10-31: 0.3315%; 2015-11-30: 0.3675%; 2015-12-31: 3.437%; 2016-01-31: 12.36%; 2016-02-29: 13.24%; 2016-03-31: 12.83%; 2016-04-30: 12.24%; 2016-05-31: 11.76%; 2016-06-30: 10.74%; 2016-07-31: 10%; 2016-08-31: 8.93%; 2016-09-30: 1.102%
|  |  |  | Cumulative % Per Above ==> | 2015-02-01: 0.9415%; 2015-03-31: 1.129%; 2015-04-30: 1.316%; 2015-05-31: 1.504%; 2015-06-30: 1.691%; 2015-07-31: 2.145%; 2015-08-31: 2.332%; 2015-09-30: 2.664%; 2015-10-31: 2.995%; 2015-11-30: 3.363%; 2015-12-31: 6.8%; 2016-01-31: 19.16%; 2016-02-29: 32.39%; 2016-03-31: 45.23%; 2016-04-30: 57.47%; 2016-05-31: 69.23%; 2016-06-30: 79.97%; 2016-07-31: 89.97%; 2016-08-31: 98.9%; 2016-09-30: 100%; 2016-10-31: 100%; 2016-11-30: 100%; 2016-12-31: 100%
|  |  |  | Monthly % Per 3 Pack B-4's ==> | 2015-06-30: 0%; 2015-07-31: 1.026%; 2015-08-31: 2.562%; 2015-09-30: 0.5798%; 2015-10-31: 7.496%; 2015-11-30: 2.038%; 2015-12-31: 0.8441%; 2016-01-31: 1.914%; 2016-02-29: 11.84%; 2016-03-31: 18.59%; 2016-04-30: 2.946%; 2016-05-31: 6.605%; 2016-06-30: 26.95%; 2016-07-31: 2.469%; 2016-08-31: 3.938%; 2016-09-30: 3.938%; 2016-10-31: 3.119%; 2016-11-30: 0.3658%; 2016-12-31: 1.04%; 2017-01-31: 0.9825%; 2017-02-28: 0.7548%; 2017-03-31: 2.295e-05%
|  |  |  | Cumulative % Per 3 Pack B-4's ==> | 2015-02-01: 0%; 2015-03-31: 0%; 2015-04-30: 0%; 2015-05-31: 0%; 2015-06-30: 0%; 2015-07-31: 1.026%; 2015-08-31: 3.588%; 2015-09-30: 4.168%; 2015-10-31: 11.66%; 2015-11-30: 13.7%; 2015-12-31: 14.55%; 2016-01-31: 16.46%; 2016-02-29: 28.3%; 2016-03-31: 46.89%; 2016-04-30: 49.84%; 2016-05-31: 56.44%; 2016-06-30: 83.39%; 2016-07-31: 85.86%; 2016-08-31: 89.8%; 2016-09-30: 93.74%; 2016-10-31: 96.86%; 2016-11-30: 97.22%; 2016-12-31: 98.26%
|  |  |  | Cumulative B-4's over/(under) Above ==> | 2015-02-01: -0.9415%; 2015-03-31: -1.129%; 2015-04-30: -1.316%; 2015-05-31: -1.504%; 2015-06-30: -1.691%; 2015-07-31: -1.119%; 2015-08-31: 1.256%; 2015-09-30: 1.505%; 2015-10-31: 8.669%; 2015-11-30: 10.34%; 2015-12-31: 7.746%; 2016-01-31: -2.697%; 2016-02-29: -4.093%; 2016-03-31: 1.663%; 2016-04-30: -7.633%; 2016-05-31: -12.79%; 2016-06-30: 3.428%; 2016-07-31: -4.105%; 2016-08-31: -9.097%; 2016-09-30: -6.262%; 2016-10-31: -3.143%; 2016-11-30: -2.777%; 2016-12-31: -1.737%
| AFUDC Factor to Base Case (Case 1) | (2) | 1.1168 | 1.1362
|  | (3) | 0.83212 | 0.80382
|  | (4) | 0.95815 | 0.95815