## calc14
OPC 012963
FPL RC-16
2014 | Form 27 Received/Wheels | [6 empty] | JEA Loss | CORONA | Station | Distribution | DATE:3/23/2015
(HOURS) | LCEC | CES | SEC | St.Lucie | Firm Transmission | NEL | FLOW TX | Payback | Loss | Service | Motor Operate switch
8760 | 3832845 | 0 | 1541845 | 1055978 | 7361153 | 116027434 | 123388587 | 19451 | 93749.1528 | 50768.0544 | 2785.1544
| (form 27) | (form 27) | (form 27) | (form 27) | FERC 1 | (NEL contains CES&FKEC | (F3+G3)
& LCEC&WACHULA& BLOUNTSTOWN )
( SCC Data included NOLOAD LOSS for GSU, AUTO, DISTRIBUTION TRANSFORMERS)
| SCC DATA 2013 LOSS | [7 empty] | Comparison: | Last Year | This Year | Difference | % change
| MONTH | GSU | LINE | AUTX | DIST | TOTAL | LESS DIST |  | NEL | 111655211 | 116027434 | 4372223 | 3.916%
| JAN | 17387 | 121211 | 13567 | 32437 | 184602 | 152165 |  | SEC Received | 4627779 | 1541845 | -3085934 | -66.68%
| FEB | 15744 | 112883 | 12544 | 30312 | 171482 | 141170 |  | St.Lucie | 1282825 | 1055978 | -226847 | -17.68%
| MAR | 17265 | 106613 | 13395 | 32473 | 169746 | 137273 |  | Transmission Firm | 9486766 | 7361153 | -2125613 | -22.41%
| APR | 18101 | 129407 | 14021 | 35283 | 196812 | 161529 |  | JEA Loss PB | 17600 | 19451 | 1851 | 10.52%
| MAY | 20712 | 163423 | 15098 | 40338 | 239571 | 199233 |  | CES | 86175 | 0 | -86175 | -100%
| JUN | 19867 | 190690 | 14885 | 40170 | 265612 | 225442 |  | LCEC | 1202149 | 3832845 | 2630696 | 218.8%
| JUL | 21450 | 194183 | 15386 | 43625 | 274644 | 231019 |  | Trans. Loss | 2320341.0498 | 2362248.2072 | 41907.1574 | 1.806%
| AUG | 22691 | 215385 | 16066 | 47649 | 301790 | 254141 |  | Dist. TX Loss | 447744.5544 | 449574.1544 | 1829.6 | 0.4086%
| SEP | 20471 | 178572 | 15062 | 41508 | 255613 | 214105 |  | Trans. Sales | 3722953.447 | 7185763 | 3462809.553 | 93.01%
| OCT | 20182 | 161093 | 14991 | 39640 | 235905 | 196265 |  | Primary Loss | 636954 | 623574 | -13380 | -2.101%
| NOV | 16649 | 122399 | 13162 | 31294 | 183505 | 152211 | Flow | To Distr. | 105611916.5032 | 106479422.7928 | 867506.2896 | 0.8214%
| DEC | 17664 | 121565 | 13947 | 32060 | 185236 | 153176 | TOTAL LOSS |  | 2768085.6042 | 2811822.3616 | 43736.7574 | 1.58%
| TOTAL | 228183 | 1817424 | 172124 | 446789 | 2664518 | 2217729
Total Adjust Yearly Loss |  | GSU | LINE | AUTX | DIST | Total Loss |  | FPL NET Generation |  | 101987156 | 107498092 | 5510936 | 5.404% | 3
|  | 228183 | 1911173.1528 | 222892.0544 | 449574.1544 | 2811822.3616 |  | Internal IPP&cogen |  | 2899402 | 3296907 | 397505 | 13.71%
|  |  | (D21+J3) | (E21+K3) | (F21+L3) | sum(C23..F23) |  | - | SJRPP | 3113757 | 3535452 | 421695 | 13.54%
[8 empty] | - | Sh#4 | 4660148 | 3066387 | -1593761 | -34.2%
TOTAL SYSTEM LOSS (MWh) = |  |  |  | 2362248.2072 |  |  |  | FPL Internal Net Generation |  | 102341128 | 110794999 | 8453871 | 8.26%
(Excluded distribution loss) |  |  |  | sum(c23..e23) | [6 empty] | (L22+L23)
[7 empty] | FERC 1 | FF-1?
TOTAL DISTRIBUTION LOSS = |  |  |  | 449574.1544 |  | SEC | 2282100 | P
(MWh) |  |  |  | (F23) |  | SL Entitlement | 586976 | P
[6 empty] | FMPA | 2485655 | P
[6 empty] | VERO | 753930 | P
% GSU LOSS | 0.206% |  |  |  |  | Reedy Creek | 18664 | P
| (C23/L27)*100 |  |  |  |  | City of Homestead(PEF) | 193026 | P
[6 empty] | City of Homestead(stanton) | 80622 | P
[6 empty] | Orlando (Pt Charlotte) | 12808 | P
[6 empty] | Okeefenokee(West Nassaw) | 56543 | P
[6 empty] | Tampa( Oleander) | 61704 | P
[6 empty] | LWU | 454102 | P
[6 empty] | NSB | 375023 | P
[6 empty] | Firm TX for other | 7361153
Prepared at direction of legal counsel.

## Trans. Letter
OPC 012964
FPL RC-16
Florida Power & Light Company
System Average Transmission Loss Percentage for 2015
(Based on 2014 Data)
1. Transmission and Conversion Losses, MWH | 2811822.3616 | Total Trans Losses (GSU and Trans) + Distr Subst Losses: Line 2 + Line 3 + Line 4
2. Generator Step-Up Transformer Loss,MWH | 228183
3. Conversion Losses (Distribution Substation), MWH | 449574.1544
4. Transmission losses (Line 1 - Line 2-Line 3), MWH | 2134065.2072
5. Southern/JEA Transfers Loss Payback, MWH | 19451 | Direct input into UI |  |  | G:[Southern/JEA Transfers Loss Payback - MWH]
6. Non-Firm Wheeling Losses, MWH | 77259 | confirmed with FF1, pages 328-330; Direct input into UI |  |  | I:[Non-Firm Wheeling Losses - MWH]
7. Short Term Firm Wheeling Losses, MWH | 54514 | confirmed with FF1, pages 328-330; Direct input into UI |  |  | J:[Short-Term Firm Wheeling Losses - MWH]
8. Adjusted Transmission losses (Line 4 - Line 5-Line6-Line7),MWH | 1982841.2072 | firm only |  | should match Adjusted Transmission Line & Substation Losses in LLS
9. Flow to Transmission (MWH) | 123160404 |  | should match Flow to Transmission in LLS
(Flow on TX - Line 2)
10. System Average Transmission Loss Percentage | 1.61% | should match LLS - energy, line 11
(Line 8 divided by Line 9)
11. System Average Transmission Loss Factors
a. (1 divided by (1 - (Line10 divided by 100))) | 1.0164 | should match LLS - energy, line 11
b. (1 - (Line 10 divided by 100)) | 0.9839
12. System Average Transmission Loss Percentage including GSU losses | 1.792%
(Line 8 + line 2) divided by( Line 9+ Line 2)
13. System Average Transmission Loss Expansion Factor including GSU losses
a. (1 divided by (1- (Line 12 divided by 100))) | 1.0182
b. (1 - (Line 12 divided by 100)) | 0.98208

## Distr. Letter
OPC 012965
FPL RC-16
Florida Power & Light Company
System Average Distribution Loss Percentage for 2015
(Based on 2014 Data)
1. Net Energy for Load, MWH |  | 116027434 | can verify with Form 27a; direct input into UI |  |  | F:[Net Energy for Load - MWH]
2. Transmission Losses & GSU Losses, MWH |  | 2362248.2072
3. Sales at Transmission, MWH | (Final number provided by Amy Zamora 2/10/2015) | 7185763 |  | Should match Delivered Sales at Transmission in LLS
(Includes CES, FKEC,LCEC,MDCSWM, Wauchula,Blountstown and Retail sales)
4. Flow to Distribution (Line 1 - Line 2 - Line 3), MWH |  | 106479422.7928 |  | Should match Flow to Distribution in LLS
5. Conversion Losses (Distribution Substation), MWH |  | 449574.1544 |  |  | Line 4 - Line 5 | 106029848.6384 | Should match Flow to Primary Lines in LLS
6. Primary Losses, MWH | (Final number provided by Amy Zamora 2/10/2015) | 623574 | from CABLE Losses; direct input into UI |  |  | 105406274.6384 | Should match Flow on Primary in LLS
|  |  | X:[Primary Line Energy Losses - MWH] |  |  | above - line 6
7. Distribution Losses (Substation and Primary Losses), MWH |  | 1073148.1544
(Line 5 + Line 6)
8. System Average Primary Distribution Loss Percentage |  | 1.008% | = (distr subst losses + primary loss) / flow to distr in LLS
(Line 7 divided by Line 4)
9. System Average Primary Distribution Loss Factor
(1 divided by (1 - (Line 8 divided by 100))) |  | 1.0102 | = flow to distr / flow on primary in LLS

## Dist. ccMail
OPC 012966
FPL RC-16
Rev0-03/12/2015
Transmission & Conversion Losses for the year 2015 ( based on data for year 2014) |  |  | PSOE- BMB
have been calculated to be as follows:
1. Generation Step-up Losses, MWH | 228183 | calculated by Transm; | Direct input into UI |  | C:[Generation Step-up Losses - MWH]
2. Transmission Losses, MWH (excluding GSU loss) | 2134065.2072 | calculated by Transm; | Direct input into UI |  | D:[Transmission Line & Substation Losses (Excl GSU Losses) - MWH]
3. Total transmission loss (Line 1+Line 2), MWH | 2362248.2072
4. Distribution Substation Transformer Losses, MWH | 449574.1544 |  | Direct input into UI |  | E:[Distribution Substation Transformer Losses - MWH]
Also for your calculations:
Net Energy to Transmission, MWH | 123388587 | (See Note 1)
Total Firm Power Wheels for others, MWH | 7361153 | (See Note 2)
Sales at Transmission, MWH | 7185763 | (See Note 3)
Notes:
1. Net Energy to Transmission is a sum of Net Energy for Load and the Total Firm Power Wheeled for others |  |  |  | generation plus ties |  | MWH
2. Total Firm Power Wheeled for others = Seminole Received on the FERC Form No.1 | [5 empty] | 2282100 | direct input into UI |  | K:[Seminole Load Received - MWH]
+ St. Lucie Entitlements Received on the FERC Form No.1 |  |  |  | 101240 | 485736 | 586976 | direct input into UI |  | L:[St. Lucie Entitlement Received - MWH]
+ FMPA Received on the FERC Form No.1 |  |  |  | 2455740 | 29915 | 2485655
+ VERO Received on the FERC Form No.1 | [5 empty] | 753930
+ Okeefenokee Received on the FERC Form No.1 | [5 empty] | 56543
+ City of Homestead ( Stanton unit in FERC Form No.1) | [5 empty] | 80622 |  | 4492077 | TF Power Wheeled for Others -
+ City of Homestead ( PEF in FERC Form No.1) | [5 empty] | 193026 |  |  | excluding Sem and PSL Entitles
+ Reedy Creek Received on the FERC Form No.1 | [5 empty] | 18664 |  | 151224 | JEA/SFP/NF Losses
+ OUC (Port Charlotte Received on the FERC Form No.1) | [5 empty] | 12808 |  | 4643301 | Power Wheeled for Others; Direct input into UI
+ LWU Received on the FERC Form No.1 | [5 empty] | 454102 |  |  | M:[Power Wheeled for Others - MWH]
+ Tampa (Oleander Received on the FERC Form No.1) | [5 empty] | 61704
+ NSB Received on the FERC Form No.1 | [5 empty] | 375023 | 7361153 |  | Should match Calculation No. 2 in LLS
3. Sales at Transmission = Retail Transmission + (FKEC/KW+LCEC+CES+Wauchula+Blountstown+Miami Dade solid waste)
(Provided by Rate & Tariff Group) | [5 empty] | per above | 7361153
0
If you have any questions concerning these figures, please call Jared Brown at (305) 442-5274.
Other FNO:
|  |  |  | Blountstown | 38156
|  |  |  | FKEC | 780489
|  |  |  | LCEC | 3832819
|  |  |  | Wauchula | 63455
Note on G37: A. Zamora: Why aren't these included in the totals? Is it because they are wholesale customers of FPL? But KWEST is embedded in FMPA...

## NF&SFP Wheels
OPC 012967
FPL RC-16
Non-Firm Transmission Wheeling Buyers 2014
Billed Company | MWh Received | MWh Delivered
Calpine Corporation | 5795 | 5688
Cargill-Alliant | 50325 | 48942
Exelon Generation, LLC | 294 | 291
Florida Municipal Power Agency | 17498 | 17174
Fortis Energy Marketing
City of Homestead | 1229 | 1221
JEA | 12 | 12
JP Morgan Ventures
City of Lakeland | 220 | 216
City of New Smyrna Beach | 15 | 15
New Hope Power Partnership | 58582 | 57597
Oglethorpe Power Corporation
Orlando Utilities Commission | 14245 | 13682
Progress Energy Florida | 16298 | 16000
Rainbow Energy | 151812 | 121016
Reedy Creek Improvement District | 476 | 474
Seminole Electric Coop. | 168570 | 165495
Southern Company Services
The Energy Authority | 134119 | 97914
Tampa Electric Company | 190818 | 187313
City of Vero Beach | 40 | 39
Energy Marketing & Trading | 680292 | 680289
TOTAL | 1490640 | 1413378
Total Excluded EMT | 810348 | 733089
Non-Firm Transmission Loss excluded EMT |  | 77259 | Analysis of Wheeling Losses
Short Term Firm - Others | 820468 | 765954
Short Term Firm - EMT | 657537 | 657537
TOTAL | 1478005 | 1423491
Firm Wheeling loss excluded EMT |  | 54514 | Analysis of Wheeling Losses

## Corona
OPC 012968
FPL RC-16
Year 2014 500 & 230kv Corona Loss Study
500kv structures |  | Corona Losses(kw/mi) |  |  | kw/mi | From SYP cir. miles
|  | A phase | B phase | C phase | total | # miles of 500kv | losses (kw) | MWH
500kv H-frame structure | no rain | 0.185 | 0.285 | 0.185 | 0.655 | 1106.13 | 724.5151 | 5991.3346
500base1.csv | light rain (.11)in/hr | 10.527 | 16.183 | 10.527 | 37.237 | 1106.13 | 41188.9628 | 20205.6576
using 1272ACSR | Insulator losses |  |  |  | 2.6611 | 1106.13 | 2943.5447 | 25785.4513
[7 empty] | Total 500kv | 51982.4434
230 kv structures |  | Corona Losses(kw/mi) |  |  | kw/mi | From SYP cir. miles
|  | A phase | B phase | C phase | total | # miles of 230kv | losses (kw) | MWH
A-88290-75'-954 | no rain | 0.02 | 0.031 | 0.02 | 0.071 | 3187.91 | 226.3416 | 1871.7184
A-88290-75'-954 | light rain (.11)in/hr | 1.158 | 1.766 | 1.158 | 4.082 | 3187.91 | 13013.0486 | 6383.6811
ALL 230Kv Lines | Insulator losses |  |  |  | 1.2 | 3187.91 | 3825.492 | 33511.3099
[7 empty] | Total 230kv= | 41766.7094
[7 empty] | Total 500kv= | 51982.4434
[7 empty] | Total all= | 93749.1528
Miles based on total circuit miles from (301) FERC Form 422 data in Vulcan.

## Sta. Svc.
OPC 012969
FPL RC-16
|  | Voltage | Autotransformers | [6 empty] | Motor |  | Station Service (MW)
Station Name | Number | Class | 500/230 | 230/138 | 230/115 | 230/69 | 138/69 | 115/69 | Autotransformers | Operators | Breakers | Basic * | AUTX | Motor Oper. | Breakers
40th Street | 55 | 138 |  |  |  |  | 1 |  | 1 | 1 | 4 | 0.0030417 | 0.030708 | 0.00014 | 0.00076
624A | 229 | 115 | [6 empty] | 0 | 1 | 2 | 0.002625 | 0 | 0.00014 | 0.00038
Airport | 301 | 138 | [6 empty] | 0 | 0 | 4 | 0.002625 | 0 | 0 | 0.00076
Alico | 390 | 230 |  | 2 |  |  |  |  | 2 | 6 | 13 | 0.0030417 | 0.061417 | 0.00084 | 0.00247
Andytown | 480 | 500 | 6 | [5 empty] | 6 | 11 | 24 | 0.0030417 | 0.18425 | 0.00154 | 0.00456
Arcadia | 63 | 69 | [6 empty] | 0 | 0 | 2 | 0.002625 | 0 | 0 | 0.00038
Arch Creek | 329 | 138 | [6 empty] | 0 | 5 | 4 | 0.002625 | 0 | 0.0007 | 0.00076
Barna | 823 | 230 |  |  | 1 |  |  |  | 1 | 0 | 7 | 0.0030417 | 0.030708 | 0 | 0.00133
Barefoot | 945 | 230 |  | 1 |  |  |  |  | 1 | 1 | 6 | 0.0030417 | 0.030708 | 0.00014 | 0.00114
Beker | 555 | 69 | [6 empty] | 0 | 0 | 2 | 0.002625 | 0 | 0 | 0.00038
Baldwin | 46 | 230 |  |  | 1 |  |  |  | 1 | 1 | 4 | 0.0030417 | 0.030708 | 0.00014 | 0.00076
Bradentown | 70 | 138 | [6 empty] | 0 | 0 | 2 | 0.002625 | 0 | 0 | 0.00038
Bradford | 395 | 230 |  | 1 | 2 |  |  |  | 3 | 5 | 10 | 0.0030417 | 0.092125 | 0.0007 | 0.0019
Brevard | 150 | 230 |  | 2 |  |  |  |  | 2 | 0 | 17 | 0.0030417 | 0.061417 | 0 | 0.00323
Bridge | 693 | 230 | [6 empty] | 0 | 0 | 4 | 0.002625 | 0 | 0 | 0.00076
Broward | 338 | 230 |  | 2 |  |  |  |  | 2 | 5 | 24 | 0.0030417 | 0.061417 | 0.0007 | 0.00456
Buckingham | 424 | 138 | [6 empty] | 0 | 3 | 4 | 0.002625 | 0 | 0.00042 | 0.00076
Bunnell | 121 | 230 |  |  | 1 |  |  |  | 1 | 0 | 7 | 0.0030417 | 0.030708 | 0 | 0.00133
C-5 | 224 | 115 | [6 empty] | 0 | 1 | 2 | 0.002625 | 0 | 0.00014 | 0.00038
Calusa | 497 | 230 | [6 empty] | 0 | 3 | 4 | 0.002625 | 0 | 0.00042 | 0.00076
Cape Canaveral P. | 216 | 230 |  |  | 2 |  |  |  | 2 | 1 | 23 | 0.0030417 | 0.061417 | 0.00014 | 0.00437
Cedar | 537 | 230 |  | 2 |  |  |  |  | 2 | 9 | 14 | 0.0030417 | 0.061417 | 0.00126 | 0.00266
Charlotte | 254 | 230 |  | 2 |  |  | 1 |  | 3 | 3 | 18 | 0.0030417 | 0.092125 | 0.00042 | 0.00342
Coco Beach | 113 | 138 | [6 empty] | 0 | 3 | 4 | 0.002625 | 0 | 0.00042 | 0.00076
Coconut Grove | 56 | 138 | [6 empty] | 0 | 0 | 3 | 0.002625 | 0 | 0 | 0.00057
Collier | 292 | 230 |  | 2 |  |  |  |  | 2 | 8 | 15 | 0.0030417 | 0.061417 | 0.00112 | 0.00285
Columbia | 232 | 115 | [6 empty] | 0 | 6 | 5 | 0.002625 | 0 | 0.00084 | 0.00095
Conservation | 806 | 500 | 6 | [5 empty] | 6 | 4 | 13 | 0.0030417 | 0.18425 | 0.00056 | 0.00247
Corbett | 613 | 500 | 3 | [5 empty] | 3 | 3 | 22 | 0.0030417 | 0.092125 | 0.00042 | 0.00418
Cortez | 118 | 138 |  | 1 |  |  |  |  | 1 | 2 | 5 | 0.0030417 | 0.030708 | 0.00028 | 0.00095
Coast | 885 | 138 |  | 1 |  |  |  |  | 1 | 2 | 4 | 0.0030417 | 0.030708 | 0.00028 | 0.00076
Cutler Plant | 93 | 138 | [6 empty] | 0 | 2 | 15 | 0.002625 | 0 | 0.00028 | 0.00285
Dade | 81 | 230 |  | 2 |  |  |  |  | 2 | 2 | 19 | 0.0030417 | 0.061417 | 0.00028 | 0.00361
Davis | 262 | 230 |  | 2 |  |  |  |  | 2 | 0 | 22 | 0.0030417 | 0.061417 | 0 | 0.00418
Daytona Beach | 35 | 115 | [6 empty] | 0 | 0 | 3 | 0.002625 | 0 | 0 | 0.00057
Deauville | 94 | 69 | [6 empty] | 0 | 1 | 0 | 0.002625 | 0 | 0.00014 | 0
Deerfield Beach | 242 | 138 | [6 empty] | 0 | 3 | 3 | 0.002625 | 0 | 0.00042 | 0.00057
Deland | 36 | 115 | [6 empty] | 0 | 2 | 3 | 0.002625 | 0 | 0.00028 | 0.00057
DORAL | 530 | 230 | [6 empty] | 0 | 0 | 3 | 0.002625 | 0 | 0 | 0.00057
Duval | 155 | 500 | 6 | [5 empty] | 6 | 7 | 25 | 0.0030417 | 0.18425 | 0.00098 | 0.00475
Eau Gallie | 136 | 138 | [6 empty] | 0 | 3 | 4 | 0.002625 | 0 | 0.00042 | 0.00076
Emerson | 580 | 230 |  | 1 |  |  |  |  | 1 | 0 | 8 | 0.0030417 | 0.030708 | 0 | 0.00152
Flagami | 141 | 230 |  | 2 |  |  |  |  | 2 | 3 | 21 | 0.0030417 | 0.061417 | 0.00042 | 0.00399
Florida City | 143 | 230 |  | 1 |  |  |  |  | 1 | 5 | 5 | 0.0030417 | 0.030708 | 0.0007 | 0.00095
Fort Myers Plant | 34 | 230 |  | 2 |  |  |  |  | 2 | 6 | 28 | 0.0030417 | 0.061417 | 0.00084 | 0.00532
FRUIT INDUSTRIE | 294 | 138 | [6 empty] | 0 | 2 | 4 | 0.002625 | 0 | 0.00028 | 0.00076
GALLOWAY | 303 | 138 |  | 1 |  |  |  |  | 1 | 2 | 5 | 0.0030417 | 0.030708 | 0.00028 | 0.00095
General Electric | 213 | 115 | [6 empty] | 0 | 1 | 2 | 0.002625 | 0 | 0.00014 | 0.00038
GERMANTOWN | 454 | 230 |  | 1 |  |  |  |  | 1 | 0 | 7 | 0.0030417 | 0.030708 | 0 | 0.00133
Gratigny | 183 | 230 |  | 1 |  |  |  |  | 1 | 4 | 9 | 0.0030417 | 0.030708 | 0.00056 | 0.00171
Greynolds | 302 | 230 |  | 1 |  |  |  |  | 1 | 5 | 8 | 0.0030417 | 0.030708 | 0.0007 | 0.00152
Grissom | 268 | 115 | [6 empty] | 0 | 1 | 1 | 0.002625 | 0 | 0.00014 | 0.00019
Haulover | 186 | 138 | [6 empty] | 0 | 0 | 2 | 0.002625 | 0 | 0 | 0.00038
Hobe | 538 | 230 |  | 2 |  |  |  |  | 2 | 5 | 8 | 0.0030417 | 0.061417 | 0.0007 | 0.00152
Hollywood | 373 | 138 | [6 empty] | 0 | 3 | 3 | 0.002625 | 0 | 0.00042 | 0.00057
Howard | 660 | 230 |  | 2 |  |  |  |  | 2 | 0 | 6 | 0.0030417 | 0.061417 | 0 | 0.00114
Indian Creek | 330 | 138 |  |  |  |  | 2 |  | 2 | 2 | 8 | 0.0030417 | 0.061417 | 0.00028 | 0.00152
Indiantown | 339 | 230 | [6 empty] | 0 | 2 | 8 | 0.002625 | 0 | 0.00028 | 0.00152
Johnson | 361 | 230 |  | 2 |  |  |  |  | 2 | 1 | 10 | 0.0030417 | 0.061417 | 0.00014 | 0.0019
Keentown | 551 | 230 |  |  |  | 1 |  |  | 1 | 0 | 3 | 0.0030417 | 0.030708 | 0 | 0.00057
Korona | 928 | 230 |  |  | 1 |  |  |  | 1 | 1 | 6 | 0.0030417 | 0.030708 | 0.00014 | 0.00114
Laudania | 434 | 230 | [6 empty] | 0 | 3 | 3 | 0.002625 | 0 | 0.00042 | 0.00057
Lauderdale Plant | 10 | 230 |  | 4 |  |  |  |  | 4 | 6 | 47 | 0.0030417 | 0.12283 | 0.00084 | 0.00893
Laurelwood | 477 | 230 |  | 2 |  |  |  |  | 2 | 9 | 14 | 0.0030417 | 0.061417 | 0.00126 | 0.00266
Levee | 495 | 500 | 6 | [5 empty] | 6 | 6 | 21 | 0.0030417 | 0.18425 | 0.00084 | 0.00399
Little River | 54 | 138 | [6 empty] | 0 | 3 | 12 | 0.002625 | 0 | 0.00042 | 0.00228
Magnolia | 1009 | 230 |  |  | 1 |  |  |  | 1 | 2 | 7 | 0.0030417 | 0.030708 | 0.00028 | 0.00133
Malabar | 210 | 230 |  | 3 |  |  |  |  | 3 | 0 | 12 | 0.0030417 | 0.092125 | 0 | 0.00228
Manatee Plant | 519 | 230 | [6 empty] | 0 | 5 | 13 | 0.002625 | 0 | 0.0007 | 0.00247
Market | 175 | 138 | [6 empty] | 0 | 0 | 4 | 0.002625 | 0 | 0 | 0.00076
Martin Plant | 50 | 500 | 3 |  |  | 1 |  |  | 4 | 5 | 35 | 0.0030417 | 0.12283 | 0.0007 | 0.00665
Miami | 1 | 230 |  | 2 |  |  | 1 |  | 3 | 0 | 21 | 0.0030417 | 0.092125 | 0 | 0.00399
Miami Beach | 5 | 138 |  |  |  |  | 1 |  | 1 | 4 | 6 | 0.0030417 | 0.030708 | 0.00056 | 0.00114
Miami Shores | 152 | 230 |  | 1 |  |  |  |  | 1 | 4 | 3 | 0.0030417 | 0.030708 | 0.00056 | 0.00057
Midway | 246 | 500 | 3 | 2 |  |  |  |  | 5 | 0 | 29 | 0.0030417 | 0.15354 | 0 | 0.00551
Millcreek | 802 | 230 |  |  | 1 |  |  |  | 1 | 0 | 5 | 0.0030417 | 0.030708 | 0 | 0.00095
Myakka | 544 | 230 |  | 1 |  |  |  |  | 1 | 2 | 5 | 0.0030417 | 0.030708 | 0.00028 | 0.00095
Naples | 78 | 138 | [6 empty] | 0 | 0 | 2 | 0.002625 | 0 | 0 | 0.00038
New River | 140 | 115 | [5 empty] | 1 | 1 | 0 | 0 | 0.0030417 | 0.030708 | 0 | 0
Normandy Beach | 305 | 138 |  |  |  |  | 1 |  | 1 | 3 | 5 | 0.0030417 | 0.030708 | 0.00042 | 0.00095
Norris | 446 | 230 |  |  | 2 |  |  |  | 2 | 4 | 9 | 0.0030417 | 0.061417 | 0.00056 | 0.00171
North Cape | 228 | 115 | [6 empty] | 0 | 1 | 2 | 0.002625 | 0 | 0.00014 | 0.00038
Oakland Park | 80 | 230 |  | 1 |  |  |  |  | 1 | 6 | 7 | 0.0030417 | 0.030708 | 0.00084 | 0.00133
Okeechobee | 65 | 69 | [6 empty] | 0 | 0 | 3 | 0.002625 | 0 | 0 | 0.00057
Okeelanta | 828 | 138 | [6 empty] | 0 | 0 | 4 | 0.002625 | 0 | 0 | 0.00076
Orange River | 482 | 500 | 3 | [5 empty] | 3 | 3 | 11 | 0.0030417 | 0.092125 | 0.00042 | 0.00209
Ormond | 95 | 115 | [6 empty] | 0 | 3 | 4 | 0.002625 | 0 | 0.00042 | 0.00076
Orsino | 220 | 115 | [6 empty] | 0 | 1 | 2 | 0.002625 | 0 | 0.00014 | 0.00038
Osceola | 831 | 138 | [6 empty] | 0 | 0 | 4 | 0.002625 | 0 | 0 | 0.00076
Osteen | 800 | 230 |  |  | 1 |  |  |  | 1 |  |  | 0.0030417 | 0.030708
OVERTOWN |  | 230 |  | 1 |  |  |  |  | 1 | 4 | 6 | 0.0030417 | 0.030708 | 0.00056 | 0.00114
Pellicer |  | 230 |  |  | 1 |  |  |  | 1 |  |  | 0.0030417 | 0.030708
PENNSUCO | 271 | 230 | [6 empty] | 0 | 3 | 4 | 0.002625 | 0 | 0.00042 | 0.00076
Plumosus | 295 | 230 |  | 1 |  |  |  |  | 1 | 3 | 8 | 0.0030417 | 0.030708 | 0.00042 | 0.00152
Poinsett | 572 | 500 | 3 | [5 empty] | 3 | 3 | 20 | 0.0030417 | 0.092125 | 0.00042 | 0.0038
Port Ever. Plant | 190 | 230 |  | 2 |  |  |  |  | 2 | 5 | 25 | 0.0030417 | 0.061417 | 0.0007 | 0.00475
Pratt & Whitney | 159 | 230 | [6 empty] | 0 | 0 | 3 | 0.002625 | 0 | 0 | 0.00057
Princeton | 86 | 230 |  | 1 |  |  |  |  | 1 | 2 | 8 | 0.0030417 | 0.030708 | 0.00028 | 0.00152
Putnam Plant | 298 | 230 |  |  | 2 |  |  |  | 2 | 3 | 21 | 0.0030417 | 0.061417 | 0.00042 | 0.00399
Railway | 360 | 138 | [6 empty] | 0 | 3 | 6 | 0.002625 | 0 | 0.00042 | 0.00114
Ranch | 25 | 230 |  | 2 |  |  |  |  | 2 | 2 | 23 | 0.0030417 | 0.061417 | 0.00028 | 0.00437
Rice | 556 | 500 | 3 | [5 empty] | 3 | 4 | 15 | 0.0030417 | 0.092125 | 0.00056 | 0.00285
Ringling | 38 | 230 |  | 2 |  |  |  |  | 2 | 4 | 21 | 0.0030417 | 0.061417 | 0.00056 | 0.00399
Riverside | 223 | 138 | [6 empty] | 0 | 5 | 6 | 0.002625 | 0 | 0.0007 | 0.00114
Riviera Plant | 73 | 138 |  | 1 |  |  |  |  | 1 | 0 | 14 | 0.0030417 | 0.030708 | 0 | 0.00266
Roberts | 1010 | 500 | 3 | [5 empty] | 3 | 7 | 5 | 0.0030417 | 0.092125 | 0.00098 | 0.00095
Roney | 435 | 69 | [6 empty] | 0 | 10 | 4 | 0.002625 | 0 | 0.0014 | 0.00076
Sandpiper | 598 | 230 |  | 1 |  |  |  |  | 1 | 1 | 3 | 0.0030417 | 0.030708 | 0.00014 | 0.00057
Sanford Plant | 30 | 230 |  |  | 2 |  |  |  | 2 | 11 | 22 | 0.0030417 | 0.061417 | 0.00154 | 0.00418
Sherman | 487 | 230 |  |  |  | 2 |  |  | 2 | 4 | 7 | 0.0030417 | 0.061417 | 0.00056 | 0.00133
Sistrunk | 462 | 230 |  | 1 |  |  |  |  | 1 | 1 | 9 | 0.0030417 | 0.030708 | 0.00014 | 0.00171
South Bay | 209 | 138 |  |  |  |  | 2 |  | 2 | 4 | 8 | 0.0030417 | 0.061417 | 0.00056 | 0.00152
South Cape | 266 | 138 |  |  |  |  | 1 |  | 1 | 4 | 5 | 0.0030417 | 0.030708 | 0.00056 | 0.00095
South Miami | 97 | 138 | [6 empty] | 0 | 4 | 6 | 0.002625 | 0 | 0.00056 | 0.00114
Springbank | 930 | 230 |  |  | 1 |  |  |  | 1 | 1 | 6 | 0.0030417 | 0.030708 | 0.00014 | 0.00114
St. John's | 545 | 230 |  |  | 1 |  |  |  | 1 | 4 | 5 | 0.0030417 | 0.030708 | 0.00056 | 0.00095
St. Lucie Plant | 403 | 230 | [6 empty] | 0 | 2 | 12 | 0.002625 | 0 | 0.00028 | 0.00228
Starke | 45 | 115 | [5 empty] | 0 | 0 | 0 | 3 | 0.002625 | 0 | 0 | 0.00057
Terry |  | 230 |  | 1 |  |  |  |  | 1 | 1 | 6 | 0.0030417 | 0.030708 | 0.00014 | 0.00114
Tocoi | 558 | 230 | [6 empty] | 0 | 3 | 3 | 0.002625 | 0 | 0.00042 | 0.00057
Turkey Point | 264 | 230 | [6 empty] | 0 | 11 | 28 | 0.002625 | 0 | 0.00154 | 0.00532
Turnpike | 601 | 230 | [6 empty] | 0 | 1 | 3 | 0.002625 | 0 | 0.00014 | 0.00057
Venetian | 179 | 69 |  |  |  |  | 1 |  | 1 | 0 | 5 | 0.0030417 | 0.030708 | 0 | 0.00095
Venice | 334 | 138 | [6 empty] | 0 | 6 | 3 | 0.002625 | 0 | 0.00084 | 0.00057
Volusia | 248 | 230 |  |  | 4 |  |  |  | 4 | 0 | 19 | 0.0030417 | 0.12283 | 0 | 0.00361
Warfield | 819 | 230 | [6 empty] | 0 | 2 | 3 | 0.002625 | 0 | 0.00028 | 0.00057
West Palm Beach | 250 | 138 |  |  |  |  | 0 |  | 0 | 4 | 15 | 0.002625 | 0 | 0.00056 | 0.00285
Whidden | 563 | 230 |  |  |  | 1 |  |  | 1 | 0 | 4 | 0.0030417 | 0.030708 | 0 | 0.00076
Yamato | 324 | 230 |  | 2 |  |  |  |  | 2 | 3 | 10 | 0.0030417 | 0.061417 | 0.00042 | 0.0019
[5 empty] | 153 |  |  |  | 153 |  | Total | 0.37112 | 4.6984 | 0.43106 | 0.29488
[9 empty] | Total Transmission Switches | Total Breakers | Total Autx |  |  | Grand Total | 5.7954
[8 empty] | 4631 | 3079 | 1552 | 153
[9 empty] | Total Distribution Switches |  | * Basic usage includes A/C for relay vault and two battery chargers for a station with transformation (otherwise only one battery charger)
2271
Power consumed by distribution motor operate
[9 empty] | 0.31794 |  | 48 | KWh/day for A/C
[11 empty] | 25 | KWh/day for 2-battery chargers
[11 empty] | 15 | KWh/day for 1-battery charger
[11 empty] | 190 | W/hr for breaker heater
[11 empty] | 140 | W/hr for motor operator heater
[11 empty] | 737 | KWh/day for auto's fans & pumps