## Avoided_Costs_Table
GT Brownfield- SIMPLE CYCLE COMBUSTION TURBINE |  | units 1 - 5
(1) Base Year |  | 2019
(2) In Service Year for Avoided Generation Unit |  | 2027-06-01
(3) Winter Capacity | MW | 233.3
(4) Base Year Avoided Generating Unit Cost (including transmission upgrade cost) | $/KW | 549.3958
(5) Generator Cost Escalation Rate |  | 1.27%
(6) Generator Fixed O&M Cost (including non-escalating gas pipeline reservation cost) | $/kw-year | 80.7888
(7) Generator Fixed O&M Cost Escalation Rate |  | 2.5%
(8) Avoided Gen Unit Variable O&M Cost | ¢/Kwh | 0.87243
(9) Generator Variable O&M Cost Escalation Rate |  | 2.5%
(10) Generator Capacity Factor |  | 1% winter 9% summer
(11) Avoided Generating Unit Fuel Cost | ¢/Kwh | 5.0169
(12) Avoided Generating Unit Fuel Escalation Rate |  | 4.647%
CC2X1 J Greenfield Combined Cycle - COMBINED CYCLE |  | unit 6
(1) Base Year |  | 2019
(2) In Service Year for Avoided Generation Unit |  | 2029-06-01
(3) Winter Capacity | MW | 1366
(4) Base Year Avoided Generating Unit Cost (including transmission upgrade cost) | $/KW | 909.6954
(5) Generator Cost Escalation Rate |  | 1.475%
(6) Generator Fixed O&M Cost (including non-escalating gas pipeline reservation cost) | $/kw-year | 84.3881
(7) Generator Fixed O&M Cost Escalation Rate |  | 2.5%
(8) Avoided Gen Unit Variable O&M Cost | ¢/Kwh | 0.57872
(9) Generator Variable O&M Cost Escalation Rate |  | 2.5%
(10) Generator Capacity Factor |  | 74% winter 87% summer
(11) Avoided Generating Unit Fuel Cost | ¢/Kwh | 3.607
(12) Avoided Generating Unit Fuel Escalation Rate |  | 4.647%
GT Brownfield- SIMPLE CYCLE COMBUSTION TURBINE |  | unit 7
(1) Base Year |  | 2019
(2) In Service Year for Avoided Generation Unit |  | 2032-06-01
(3) Winter Capacity | MW | 233.3
(4) Base Year Avoided Generating Unit Cost (including transmission upgrade cost) | $/KW | 549.3958
(5) Generator Cost Escalation Rate |  | 1.27%
(6) Generator Fixed O&M Cost (including non-escalating gas pipeline reservation cost) | $/kw-year | 91.4051
(7) Generator Fixed O&M Cost Escalation Rate |  | 2.5%
(8) Avoided Gen Unit Variable O&M Cost | ¢/Kwh | 0.98708
(9) Generator Variable O&M Cost Escalation Rate |  | 2.5%
(10) Generator Capacity Factor |  | 1% winter 9% summer
(11) Avoided Generating Unit Fuel Cost | ¢/Kwh | 7.1757
(12) Avoided Generating Unit Fuel Escalation Rate |  | 4.647%
GT Avg- SIMPLE CYCLE COMBUSTION TURBINE |  | unit 8
(1) Base Year |  | 2019
(2) In Service Year for Avoided Generation Unit |  | 2033-06-01
(3) Winter Capacity | MW | 233.3
(4) Base Year Avoided Generating Unit Cost (including transmission upgrade cost) | $/KW | 619.1446
(5) Generator Cost Escalation Rate |  | 1.27%
(6) Generator Fixed O&M Cost (including non-escalating gas pipeline reservation cost) | $/kw-year | 96.1316
(7) Generator Fixed O&M Cost Escalation Rate |  | 2.5%
(8) Avoided Gen Unit Variable O&M Cost | ¢/Kwh | 1.0118
(9) Generator Variable O&M Cost Escalation Rate |  | 2.5%
(10) Generator Capacity Factor |  | 1% winter 9% summer
(11) Avoided Generating Unit Fuel Cost | ¢/Kwh | 7.5404
(12) Avoided Generating Unit Fuel Escalation Rate |  | 4.647%
GT Avg- SIMPLE CYCLE COMBUSTION TURBINE |  | units 9 and 10
(1) Base Year |  | 2019
(2) In Service Year for Avoided Generation Unit |  | 2034-06-01
(3) Winter Capacity | MW | 233.3
(4) Base Year Avoided Generating Unit Cost (including transmission upgrade cost) | $/KW | 619.1446
(5) Generator Cost Escalation Rate |  | 1.27%
(6) Generator Fixed O&M Cost (including non-escalating gas pipeline reservation cost) | $/kw-year | 98.5349
(7) Generator Fixed O&M Cost Escalation Rate |  | 2.5%
(8) Avoided Gen Unit Variable O&M Cost | ¢/Kwh | 1.037
(9) Generator Variable O&M Cost Escalation Rate |  | 2.5%
(10) Generator Capacity Factor |  | 1% winter 9% summer
(11) Avoided Generating Unit Fuel Cost | ¢/Kwh | 7.79
(12) Avoided Generating Unit Fuel Escalation Rate |  | 4.647%
CC2X1 J Greenfield Combined Cycle - COMBINED CYCLE |  | unit 11
(1) Base Year |  | 2019
(2) In Service Year for Avoided Generation Unit |  | 2035-06-01
(3) Winter Capacity | MW | 1366
(4) Base Year Avoided Generating Unit Cost (including transmission upgrade cost) | $/KW | 909.6954
(5) Generator Cost Escalation Rate |  | 1.475%
(6) Generator Fixed O&M Cost (including non-escalating gas pipeline reservation cost) | $/kw-year | 97.8643
(7) Generator Fixed O&M Cost Escalation Rate |  | 2.5%
(8) Avoided Gen Unit Variable O&M Cost | ¢/Kwh | 0.67114
(9) Generator Variable O&M Cost Escalation Rate |  | 2.5%
(10) Generator Capacity Factor |  | 74% winter 87% summer
(11) Avoided Generating Unit Fuel Cost | ¢/Kwh | 4.5091
(12) Avoided Generating Unit Fuel Escalation Rate |  | 4.647%
GT Avg- SIMPLE CYCLE COMBUSTION TURBINE |  | units 12 and 13
(1) Base Year |  | 2019
(2) In Service Year for Avoided Generation Unit |  | 2035-06-01
(3) Winter Capacity | MW | 233.3
(4) Base Year Avoided Generating Unit Cost (including transmission upgrade cost) | $/KW | 619.1446
(5) Generator Cost Escalation Rate |  | 1.27%
(6) Generator Fixed O&M Cost (including non-escalating gas pipeline reservation cost) | $/kw-year | 100.9983
(7) Generator Fixed O&M Cost Escalation Rate |  | 2.5%
(8) Avoided Gen Unit Variable O&M Cost | ¢/Kwh | 1.063
(9) Generator Variable O&M Cost Escalation Rate |  | 2.5%
(10) Generator Capacity Factor |  | 1% winter 9% summer
(11) Avoided Generating Unit Fuel Cost | ¢/Kwh | 7.4022
(12) Avoided Generating Unit Fuel Escalation Rate |  | 4.647%
GT Avg- SIMPLE CYCLE COMBUSTION TURBINE |  | unit 14
(1) Base Year |  | 2019
(2) In Service Year for Avoided Generation Unit |  | 2037-06-01
(3) Winter Capacity | MW | 233.3
(4) Base Year Avoided Generating Unit Cost (including transmission upgrade cost) | $/KW | 619.1446
(5) Generator Cost Escalation Rate |  | 1.27%
(6) Generator Fixed O&M Cost (including non-escalating gas pipeline reservation cost) | $/kw-year | 106.1113
(7) Generator Fixed O&M Cost Escalation Rate |  | 2.5%
(8) Avoided Gen Unit Variable O&M Cost | ¢/Kwh | 1.1168
(9) Generator Variable O&M Cost Escalation Rate |  | 2.5%
(10) Generator Capacity Factor |  | 1% winter 9% summer
(11) Avoided Generating Unit Fuel Cost | ¢/Kwh | 7.8648
(12) Avoided Generating Unit Fuel Escalation Rate |  | 4.647%
GT Avg- SIMPLE CYCLE COMBUSTION TURBINE |  | units 15 and 16
(1) Base Year |  | 2019
(2) In Service Year for Avoided Generation Unit |  | 2038-06-01
(3) Winter Capacity | MW | 233.3
(4) Base Year Avoided Generating Unit Cost (including transmission upgrade cost) | $/KW | 619.1446
(5) Generator Cost Escalation Rate |  | 1.27%
(6) Generator Fixed O&M Cost (including non-escalating gas pipeline reservation cost) | $/kw-year | 108.7641
(7) Generator Fixed O&M Cost Escalation Rate |  | 2.5%
(8) Avoided Gen Unit Variable O&M Cost | ¢/Kwh | 1.1447
(9) Generator Variable O&M Cost Escalation Rate |  | 2.5%
(10) Generator Capacity Factor |  | 1% winter 9% summer
(11) Avoided Generating Unit Fuel Cost | ¢/Kwh | 8.4676
(12) Avoided Generating Unit Fuel Escalation Rate |  | 4.647%
GT Avg- SIMPLE CYCLE COMBUSTION TURBINE |  | unit 17
(1) Base Year |  | 2019
(2) In Service Year for Avoided Generation Unit |  | 2040-06-01
(3) Winter Capacity | MW | 233.3
(4) Base Year Avoided Generating Unit Cost (including transmission upgrade cost) | $/KW | 619.1446
(5) Generator Cost Escalation Rate |  | 1.27%
(6) Generator Fixed O&M Cost (including non-escalating gas pipeline reservation cost) | $/kw-year | 114.2703
(7) Generator Fixed O&M Cost Escalation Rate |  | 2.5%
(8) Avoided Gen Unit Variable O&M Cost | ¢/Kwh | 1.2027
(9) Generator Variable O&M Cost Escalation Rate |  | 2.5%
(10) Generator Capacity Factor |  | 1% winter 9% summer
(11) Avoided Generating Unit Fuel Cost | ¢/Kwh | 9.3189
(12) Avoided Generating Unit Fuel Escalation Rate |  | 4.647%
GT Avg- SIMPLE CYCLE COMBUSTION TURBINE |  | unit 18
(1) Base Year |  | 2019
(2) In Service Year for Avoided Generation Unit |  | 2041-06-01
(3) Winter Capacity | MW | 233.3
(4) Base Year Avoided Generating Unit Cost (including transmission upgrade cost) | $/KW | 619.1446
(5) Generator Cost Escalation Rate |  | 1.27%
(6) Generator Fixed O&M Cost (including non-escalating gas pipeline reservation cost) | $/kw-year | 117.1271
(7) Generator Fixed O&M Cost Escalation Rate |  | 2.5%
(8) Avoided Gen Unit Variable O&M Cost | ¢/Kwh | 1.2327
(9) Generator Variable O&M Cost Escalation Rate |  | 2.5%
(10) Generator Capacity Factor |  | 1% winter 9% summer
(11) Avoided Generating Unit Fuel Cost | ¢/Kwh | 9.5515
(12) Avoided Generating Unit Fuel Escalation Rate |  | 4.647%
GT Avg- SIMPLE CYCLE COMBUSTION TURBINE |  | unit 19
(1) Base Year |  | 2019
(2) In Service Year for Avoided Generation Unit |  | 2043-06-01
(3) Winter Capacity | MW | 233.3
(4) Base Year Avoided Generating Unit Cost (including transmission upgrade cost) | $/KW | 619.1446
(5) Generator Cost Escalation Rate |  | 1.27%
(6) Generator Fixed O&M Cost (including non-escalating gas pipeline reservation cost) | $/kw-year | 123.0566
(7) Generator Fixed O&M Cost Escalation Rate |  | 2.5%
(8) Avoided Gen Unit Variable O&M Cost | ¢/Kwh | 1.2951
(9) Generator Variable O&M Cost Escalation Rate |  | 2.5%
(10) Generator Capacity Factor |  | 1% winter 9% summer
(11) Avoided Generating Unit Fuel Cost | ¢/Kwh | 10.0337
(12) Avoided Generating Unit Fuel Escalation Rate |  | 4.647%
Note: all the fixed cost, variable and fuel costs are nominal dollar value in the first year when unit is in service