## WLU
2019 | Jan Used | Jan Loss | Feb Used | Feb Loss | March Used | March Loss | April Used | April Loss | May Used | May Loss | June Used | June Loss | July Used | July Loss | Aug Used | Aug Loss | Sept Used | Sept Loss | Oct Used | Oct Loss | Nov Used | Nov Loss | Dec Used | Dec Loss | YTD Total
Park Ridge | 0.00763 | 0 | 0.00805 | 0 | 0.00773 | 0 | 0.00783 | 0 | 0.00775 | 0 | 0.00809 | 0 | 0.00792 | 0 | 0.00828 | 0 | 0.00803 | 0 | 0.00775 | 0 | 0.008326 | 0 | 0.00775 | 0 | 0.095136
Total | 0.00763 |  | 0.00805 |  | 0.00773 |  | 0.00783 |  | 0.00775 |  | 0.00809 |  | 0.00792 |  | 0.00828 |  | 0.00803 |  | 0.00775 |  | 0.008326 |  | 0.00775

## Sheet1
System | 2019-01-01 | 2019-02-01 | 2019-03-01 | 2019-04-01 | 2019-05-01 | 2019-06-01 | 2019-07-01 | 2019-08-01 | 2019-09-17 | 2019-10-17 | 2019-11-17 | 2019-12-17
Park Ridge | 485700 | 475100 | 520800 | 519000 | 590000 | 592100 | 555800 | 539600 | 526700 | 499000 | 496600 | 492900

## Park Ridge
252/312 - Park Ridge
PWS ID No. 3590993
CUP No. 20-117-8353-3 |  | Exp. 11/15/20
FDEP Permitted Max Day Capacity of Plant - .246 mgd
Hyper Links'!A1
|  |  |  | Total Water Used/Loss |  |  |  |  | Source Mtr Error Adj. 04-19-18 -1.01% 02/21/19 -2.04%
| Pumped | Pumped Daily Avg. | Pumped Daily Max. | Gallons Used | Gallons Loss | Total Used/ Loss | Pumped, Less Gallons Loss/Used | Billed Consumption | Meter Adj. % | Pumped Meter Adj. | Pumped + Source Mtr Error, - Gals Loss/Use | Total AFW (Total Used/Loss + Billed) | AFW % plus source mtr. error | 2018 AFW %
January 2019 | 0.4857 | 0.015668 | 0.0236 | 0.00763 | 0 | 0.00763 | 0.47807 | 0.45979 | -1.01% | -0.0049056 | 0.47316 | 0.46742 | 97.22% | 101.8%
February | 0.4751 | 0.016968 | 0.0264 | 0.00805 | 0 | 0.00805 | 0.46705 | 0.47443 | -1.01% -2.04% | -0.0056737 | 0.46138 | 0.48248 | 102.8% | 96.54%
March | 0.5208 | 0.0168 | 0.0263 | 0.00773 | 0 | 0.00773 | 0.51307 | 0.50462 | -2.04% | -0.010624 | 0.50245 | 0.51235 | 100.4% | 96.23%
April | 0.519 | 0.0173 | 0.0245 | 0.00783 | 0 | 0.00783 | 0.51117 | 0.50762 | -2.04% | -0.010588 | 0.50058 | 0.51545 | 101.4% | 101.4%
May | 0.59 | 0.019032 | 0.0299 | 0.00775 | 0 | 0.00775 | 0.58225 | 0.55128 | -2.04% | -0.012036 | 0.57021 | 0.55903 | 96.72% | 105.3%
June | 0.5921 | 0.019737 | 0.0286 | 0.00809 | 0 | 0.00809 | 0.58401 | 0.50277 | -2.04% | -0.012079 | 0.57193 | 0.51086 | 88.08% | 96.33%
July | 0.5558 | 0.017929 | 0.0236 | 0.00792 | 0 | 0.00792 | 0.54788 | 0.52825 | -2.04% | -0.011338 | 0.53654 | 0.53617 | 98.48% | 100.3%
August | 0.5396 | 0.017406 | 0.0225 | 0.00828 | 0 | 0.00828 | 0.53132 | 0.49322 | -2.04% | -0.011008 | 0.52031 | 0.5015 | 94.87% | 97.25%
September | 0.5267 | 0.017557 | 0.0262 | 0.00803 | 0 | 0.00803 | 0.51867 | 0.51901 | -2.04% | -0.010745 | 0.50793 | 0.52704 | 102.1% | 98.32%
October | 0.499 | 0.016097 | 0.0232 | 0.00775 | 0 | 0.00775 | 0.49125 | 0.49416 | -2.04% | -0.01018 | 0.48107 | 0.50191 | 102.7% | 100.1%
November | 0.4966 | 0.016553 | 0.0215 | 0.008326 | 0 | 0.008326 | 0.48827 | 0.49149 | -2.04% | -0.010131 | 0.47814 | 0.49982 | 102.7% | 99.47%
December | 0.4929 | 0.0159 | 0.0213 | 0.00775 | 0 | 0.00775 | 0.48515 | 0.47203 | -2.04% | -0.010055 | 0.47509 | 0.47978 | 99.37% | 99.68%
YTD Total/Avg/Max | 6.2933 | 0.017246 | 0.0299 | 0.095136 | 0 | 0.095136 | 6.1982 | 5.9987 | -2.04% | -0.11936 | 6.0788 | 6.0938
| 6.2933 | [8 empty] | -0.11936 |  | 6.0938
| 0 | Proof to Daily Flow |  |  |  |  | Proof to Total Billed | 0 |  |  |  | YTD AFW% Jan-Dec | 98.7%
Water Loss-Use'!A1
[5 empty] | Water Loss/Use Proof | 0
Verif W/UIWtrMn WLU wrksht & WAF Input
Source Mtr Error Adj. 04-19-18 -1.01% 02/21/19 -2.04%
[10 empty] | Dates | Meter Adj. % | Pumped | Adjusted
[10 empty] | 02/01-02/21 | -1.01% | 0.3323 | -0.0033562
[10 empty] | 02/22-02/28 | -2.04% | 0.1136 | -0.0023174
-0.0056737
Note on B7: Picked up from Daily Flow. Total daily flow, Column AH
Note on C7: Picked up from Daily Flow AVG, Column AI
Note on D7: Picked up from Daily Flow MAX, Column AJ
Note on E7: Click on the hyperlink at the top of this worksheet to access the Water Accountability Data Input Form for the used detail.
Note on F7: Click on the hyperlink at the top of this worksheet to access the Water Accountability Data Input Form for the loss detail.

## Daily Flow-312
252/312 - Park Ridge |  |  |  |  | MWAF - link to AH(x) |  |  |  |  | Hyper Links'!A1
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg. | Max | Proof
2019-01-01 | 0.0141 | 0.0236 | 0.0094 | 0.014 | 0.0145 | 0.0176 | 0.0176 | 0.0165 | 0.0142 | 0.0164 | 0.0116 | 0.0146 | 0.0203 | 0.0203 | 0.0145 | 0.0147 | 0.0093 | 0.0161 | 0.0166 | 0.0182 | 0.0182 | 0.0187 | 0.0169 | 0.0161 | 0.0141 | 0.0118 | 0.0172 | 0.0172 | 0.0138 | 0.0115 | 0.0161 | 0.4857 | 0.015668 | 0.0236 | 0
February | 0.0138 | 0.016 | 0.0179 | 0.0179 | 0.0183 | 0.0098 | 0.0211 | 0.0119 | 0.0193 | 0.021 | 0.021 | 0.0191 | 0.0163 | 0.0138 | 0.0118 | 0.0163 | 0.0188 | 0.0188 | 0.0138 | 0.0264 | 0.0184 | 0.0141 | 0.0167 | 0.018 | 0.018 | 0.0141 | 0.0189 | 0.0138 |  |  |  | 0.4751 | 0.016968 | 0.0264 | 0
March | 0.0115 | 0.0117 | 0.0263 | 0.0263 | 0.0165 | 0.01 | 0.0161 | 0.0208 | 0.0137 | 0.0178 | 0.0178 | 0.0186 | 0.0165 | 0.0179 | 0.0154 | 0.0217 | 0.0163 | 0.0163 | 0.0185 | 0.0168 | 0.0141 | 0.0138 | 0.0147 | 0.0212 | 0.0212 | 0.0115 | 0.0163 | 0.0138 | 0.0186 | 0.0111 | 0.018 | 0.5208 | 0.0168 | 0.0263 | 0
April | 0.018 | 0.0165 | 0.0182 | 0.0116 | 0.0186 | 0.0112 | 0.0164 | 0.0164 | 0.0162 | 0.0163 | 0.0138 | 0.0139 | 0.0184 | 0.0168 | 0.0168 | 0.0142 | 0.0214 | 0.0188 | 0.0137 | 0.0163 | 0.0191 | 0.0191 | 0.0137 | 0.0193 | 0.0192 | 0.0139 | 0.0184 | 0.0245 | 0.0245 | 0.0238 |  | 0.519 | 0.0173 | 0.0245 | 0
May | 0.027 | 0.0139 | 0.0111 | 0.0178 | 0.0166 | 0.0166 | 0.0186 | 0.0164 | 0.0185 | 0.012 | 0.0167 | 0.0193 | 0.0193 | 0.0153 | 0.0165 | 0.0143 | 0.0142 | 0.0189 | 0.0235 | 0.0235 | 0.0166 | 0.0197 | 0.0238 | 0.0143 | 0.0184 | 0.0255 | 0.0255 | 0.022 | 0.0299 | 0.0224 | 0.0219 | 0.59 | 0.019032 | 0.0299 | 0
June | 0.0241 | 0.0262 | 0.0262 | 0.0177 | 0.0286 | 0.0165 | 0.0167 | 0.0163 | 0.0193 | 0.0193 | 0.0215 | 0.0193 | 0.021 | 0.0188 | 0.0174 | 0.0195 | 0.0195 | 0.0185 | 0.0213 | 0.0148 | 0.0186 | 0.0164 | 0.0203 | 0.0203 | 0.0165 | 0.0176 | 0.0208 | 0.0189 | 0.0202 | 0.02 |  | 0.5921 | 0.019737 | 0.0286 | 0
July | 0.02 | 0.0138 | 0.0167 | 0.0189 | 0.0191 | 0.0208 | 0.0191 | 0.0191 | 0.0166 | 0.019 | 0.0189 | 0.0185 | 0.0146 | 0.0206 | 0.0206 | 0.0191 | 0.0218 | 0.0181 | 0.0165 | 0.0119 | 0.0206 | 0.0206 | 0.021 | 0.0152 | 0.0138 | 0.0163 | 0.0162 | 0.0235 | 0.0236 | 0.0089 | 0.0124 | 0.5558 | 0.017929 | 0.0236 | 0
August | 0.0164 | 0.0162 | 0.0139 | 0.0168 | 0.0168 | 0.02 | 0.0189 | 0.0145 | 0.0165 | 0.0188 | 0.0205 | 0.0205 | 0.0135 | 0.0189 | 0.0165 | 0.0164 | 0.0189 | 0.0194 | 0.0195 | 0.012 | 0.0193 | 0.0189 | 0.0167 | 0.0122 | 0.019 | 0.019 | 0.0187 | 0.0147 | 0.014 | 0.0225 | 0.0197 | 0.5396 | 0.017406 | 0.0225 | 0
September | 0.0185 | 0.0185 | 0.0147 | 0.0188 | 0.0185 | 0.0165 | 0.0093 | 0.0214 | 0.0214 | 0.0238 | 0.0189 | 0.0119 | 0.014 | 0.0141 | 0.0178 | 0.0173 | 0.0208 | 0.0143 | 0.0262 | 0.0145 | 0.0116 | 0.0202 | 0.0202 | 0.021 | 0.019 | 0.0116 | 0.0215 | 0.0144 | 0.018 | 0.018 |  | 0.5267 | 0.017557 | 0.0262 | 0
October | 0.0188 | 0.0166 | 0.0194 | 0.0166 | 0.0141 | 0.0165 | 0.0165 | 0.0161 | 0.0116 | 0.0137 | 0.0163 | 0.0166 | 0.0177 | 0.0177 | 0.0186 | 0.0167 | 0.0185 | 0.0116 | 0.0138 | 0.0164 | 0.0164 | 0.0156 | 0.0124 | 0.0232 | 0.014 | 0.0139 | 0.0163 | 0.0163 | 0.0142 | 0.0191 | 0.0138 | 0.499 | 0.016097 | 0.0232 | 0
November | 0.014 | 0.0143 | 0.0177 | 0.0177 | 0.019 | 0.0165 | 0.0144 | 0.0166 | 0.0189 | 0.018 | 0.0175 | 0.0167 | 0.0161 | 0.0124 | 0.0117 | 0.0165 | 0.0189 | 0.0189 | 0.0139 | 0.0162 | 0.0165 | 0.0116 | 0.0207 | 0.0186 | 0.0186 | 0.0165 | 0.0163 | 0.0163 | 0.0215 | 0.0141 |  | 0.4966 | 0.016553 | 0.0215 | 0
December | 0.0201 | 0.0201 | 0.018 | 0.0141 | 0.0162 | 0.0165 | 0.0116 | 0.0191 | 0.0191 | 0.0164 | 0.0163 | 0.0165 | 0.0115 | 0.0114 | 0.015 | 0.015 | 0.0185 | 0.0164 | 0.014 | 0.0139 | 0.0115 | 0.0153 | 0.0153 | 0.0167 | 0.0187 | 0.0213 | 0.0141 | 0.0114 | 0.0178 | 0.0148 | 0.0163 | 0.4929 | 0.0159 | 0.0213 | 0
Minimum | 0.0115 | 0.0117 | 0.0094 | 0.0116 | 0.0141 | 0.0098 | 0.0093 | 0.0119 | 0.0116 | 0.012 | 0.0116 | 0.0119 | 0.0115 | 0.0114 | 0.0117 | 0.0142 | 0.0093 | 0.0116 | 0.0137 | 0.0119 | 0.0115 | 0.0116 | 0.0124 | 0.0122 | 0.0138 | 0.0115 | 0.0141 | 0.0114 | 0.0138 | 0.0089 | 0.0124 | 6.2933 | Grand Total