## F 1
Gallons of Water Pumped, Sold and Unaccounted For | [8 empty] | Florida Public Service Commission
In Thousands of Gallons
Schedule F-1
Company: Utilities, Inc. of Florida - Labrador | [8 empty] | Page 1 of 1
Docket No.: 20200139-WS | [8 empty] | Preparer: Seidman, F.
Test Year Ended: December 31, 2019
Explanation: Provide a schedule of gallons of water pumped, sold and unaccounted for each month of the test
year. The gallons pumped should match the flows shown on the monthly operating reports sent to DEP. The other
uses may include plant use, flushing of hydrants and water and sewer lines, line breakages and fire flows.
Provide all calculations to substantiate the other uses. If unaccounted for water is greater than 10%, pro-
vide an explanation as to the reasons why; if less than 10%, then Columns 4 & 5 may be omitted.
_ | _ | _ | _ |  | _ | _ | _ | _ | _ | _ | _ | _
|  | (1) |  |  |  | (2) |  | (3) |  | (4) |  | (5) | (6)
[12 empty] | Unaccounted | %
Month/ |  | Total Gallons |  | Total Gallons |  | Gallons |  | Gallons |  | Other |  | For Water | Unaccounted
Year |  | Pumped |  | Corrected for |  | Purchased |  | Sold |  | Uses (2) |  | (1)+(2)-(3)-(4) | For Water
_ |  | Per MORs |  | Meter Error (1) |  |  |  | _ |  | _ |  | _ | _
2019-01-01 |  | 2.428 |  | 2.4609 |  | 0 |  | 2.0172 |  | 0.068025 |  | 0.37568 | 15.27%
2019-02-01 |  | 2.424 |  | 2.456 |  | 0 |  | 2.4805 |  | 0.06642 |  | -0.090945 | -3.703%
2019-03-01 |  | 2.794 |  | 2.8311 |  | 0 |  | 2.2668 |  | 0.056195 |  | 0.5081 | 17.95%
2019-04-01 |  | 2.062 |  | 2.0888 |  | 0 |  | 2.4407 |  | 0.020375 |  | -0.37221 | -17.82%
2019-05-01 |  | 1.517 |  | 1.514 |  | 0 |  | 1.7301 |  | 0.06526 |  | -0.2814 | -18.59%
2019-06-01 |  | 1.312 |  | 1.2728 |  | 0 |  | 1.2911 |  | 0.07867 |  | -0.09702 | -7.623%
2019-07-01 |  | 1.312 |  | 1.2728 |  | 0 |  | 1.2431 |  | 0.03476 |  | -0.005136 | -0.4035%
2019-08-01 |  | 1.322 |  | 1.2814 |  | 0 |  | 1.0637 |  | 0.03306 |  | 0.18467 | 14.41%
2019-09-01 |  | 1.669 |  | 1.619 |  | 0 |  | 1.3054 |  | 0.1872 |  | 0.12642 | 7.808%
2019-10-01 |  | 1.687 |  | 1.6367 |  | 0 |  | 1.6552 |  | 0.06203 |  | -0.08055 | -4.921%
2019-11-01 |  | 2.1025 |  | 2.0395 |  | 0 |  | 1.5334 |  | 0.083238 |  | 0.42281 | 20.73%
2019-12-01 |  | 2.2465 |  | 2.1792 |  | 0 |  | 1.9164 |  | 0.088042 |  | 0.17474 | 8.019%
|  | - |  |  |  | - |  | - |  | - |  | - | -
Total |  | 22.876 |  | 22.6521 |  | 0 |  | 20.9437 |  | 0.84327 |  | 0.86515 | 3.819%
|  | = |  |  |  | = |  | = |  | = |  | = | =
(Above data in millions of gallons)
(1) The Utility does an annual flow meter calibration. A correction factor is calculated that reflects the difference between our flow meter and a strap-on meter positioned directly adjacent to our meter to give highest confidence of meter accuracy. Meters are not necessarily repaired or modified after a calibration test. Instead, it is assumed that the measured error will be present consistently thereafter or until a subsequent flow test indicates otherwise. The corrected gallons = the gallons reported in the MOR + the percent correction determined in the most recent calibration.
(2) Other Uses includes such uses as line breaks, flushing and water quality testing
[14 empty] | 0.001 | 0.00581%

## F 2
Gallons of Wastewater Treated | [8 empty] | Florida Public Service Commission
In Thousands of Gallons
Schedule F-2
Company: Utilities, Inc. of Florida - Labrador | [8 empty] | Page 1 of 1
Docket No.: 20200139-WS | [8 empty] | Preparer: Seidman, F.
Test Year Ended: December 31, 2019
Explanation: Provide a schedule of gallons of wastewater treated by individual plant for each month of the
historical test year. Flow data should match the monthly operating reports sent to DEP.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
|  | (1) |  | (2) |  | (3) |  | (4) |  | (5) |  | (6)
|  |  |  | Individual Plant Flows | [7 empty] | Total Purch.
Month/ |  | _ | _ | _ | _ | _ | _ | _ |  | Total Plant |  | Sewage
Year |  | Forest |  | (Name) |  | (Name) |  | (Name) |  | Flows |  | Treatment
_ |  | Lakes |  | _ |  | _ |  | _ |  | _ |  | _
2019-01-01 |  | 2.1425 | [7 empty] | 2.1425 |  | 0
2019-02-01 |  | 2.6485 | [7 empty] | 2.6485 |  | 0
2019-03-01 |  | 2.6858 | [7 empty] | 2.6858 |  | 0
2019-04-01 |  | 1.8019 | [7 empty] | 1.8019 |  | 0
2019-05-01 |  | 1.1363 | [7 empty] | 1.1363 |  | 0
2019-06-01 |  | 1.2147 | [7 empty] | 1.2147 |  | 0
2019-07-01 |  | 1.6937 | [7 empty] | 1.6937 |  | 0
2019-08-01 |  | 2.5071 | [7 empty] | 2.5071 |  | 0
2019-09-01 |  | 1.5511 | [7 empty] | 1.5511 |  | 0
2019-10-01 |  | 1.824 | [7 empty] | 1.824 |  | 0
2019-11-01 |  | 2.0463 | [7 empty] | 2.0463 |  | 0
2019-12-01 |  | 1.9293 | [7 empty] | 1.9293 |  | 0
|  | - |  | - |  | - |  | - |  | - |  | -
Total |  | 23.1812 | [7 empty] | 23.1812 |  | 0
|  | = |  | = |  | = |  | = |  | = |  | =

## F 3
Water Treatment Plant Data | [6 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida - Labrador | [6 empty] | Schedule F-3
Docket No.: 20200139-WS | [6 empty] | Page 1 of 1
Test Year Ended: December 31, 2019 | [6 empty] | Preparer: Seidman, F.
Explanation: Provide the following information for each water treatment plant. If the system has water plants that
are interconnected, the data for these plants may be combined. All flow data must be obtained from the monthly oper-
ating reports (MORs) sent to the Department of Environmental Protection.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
[9 empty] | Date | GPD
1 | Plant Capacity
| The hydraulic rated capacity. If different from that shown | [5 empty] | per Sanitary Survey |  |  | 288000
| on the DEP operating or construction permit, provide an explanation. | [5 empty] | per CUP, AADF |  |  | 99785
2 | Maximum Day
| The single day with the highest pumpage rate for the test year. | [7 empty] | 2019-09-16 | 135000
Explain, on a separate sheet of paper if fire flow, line breaks,
or other unusual occurrences affected the flow this day.
3 | Five Day Max. Year
| The five days with the highest pumpage rate from any one month | [6 empty] | (1) | 2019-03-22 | 111000
| in the test year. Provide an explanation if fire flow, line | [6 empty] | (2) | 2019-03-01 | 120000
| breaks or other unusual occurrences affected the flows on | [6 empty] | (3) | 2019-03-29 | 120000
| these days. | [6 empty] | (4) | 2019-03-15 | 122000
[8 empty] | (5) | 2019-03-08 | 124000
[9 empty] | AVERAGE | 119400
[9 empty] | Max Month | 91326.3548
4 | Average Daily Flow | [7 empty] | Annual | 62060.5233
5 | Required Fire Flow | [7 empty] | * 500 gpm for 2 hours
The standards will be those as set by the Insurance Service
Organization or by a governmental agency ordinance. Provide
documents to support this calculation.

## F 4
Wastewater Treatment Plant Data | [8 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida - Labrador | [8 empty] | Schedule F-4
Docket No.: 20200139-WS | [8 empty] | Page 1 of 1
Test Year Ended: December 31, 2019 | [8 empty] | Preparer: Seidman, F.
Explanation: Provide the following information for each wastewater treatment plant. All flow data must be obtained
from the monthly operating reports (MORs) sent to the Department of Environmental Protection.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
|  |  |  | MONTH |  | GPD
1. | Plant Capacity (3MRADF) |  |  |  |  | 216000
The hydraulic rated capacity. If different from that shown on the DEP operating or construction permit, provide an explanation.
2. | Maximum 3MRADF |  |  | 3/2019 |  | 83446.9662
3 | Average Annual Daily Flow |  |  |  |  | 63510.137
An average of the daily flows during the peak usage month during the test year. Explain, on a separate page, if this peak-month was influenced by abnormal infiltration due to rainfall periods.

## F 5
Used and Useful Calculations |  |  |  |  | Florida Public Service Commission
Water Treatment Plant
Company: Utilities, Inc. of Florida - Labrador |  |  |  |  | Schedule F-5
Docket No.: 20200139-WS |  |  |  |  | Page 1 of 1
Test Year Ended: December 31, 2019 |  |  |  |  | Preparer: Seidman, F.
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the water treatment plant(s) for the historical test year and
the projected test year (if applicable).
Recap Schedules: A-5,A-9,B-13
INPUT INFORMATION:
| Total well pumping capacity, gpm |  |  |  | 1075 | gpm
| Firm Reliable well pumping capacity (largest well out), gpm |  |  |  | 200 | gpm
| Ground storage capacity, gal. |  |  |  | 34000 | gallons
| Usable ground storage (90%), gal. |  |  |  | 30600 | gallons
| Elevated Storage |  |  |  | 0 | gallons
| Usable ground storage (100%), gal. |  |  |  | 0 | gallons
| Hydropneumatic storage capacity, gal. |  |  |  | 0 | gallons
| Usable hydropneumatic storage capacity (0.00%), gal. |  |  |  | 0 | gallons
| Total usable storage, gal. |  |  |  | 30600 | gallons
| Maximum day demand, |  |  |  | 135000 | gpd
| Peak hour demand = 2x max day/1440 |  |  |  | 187.5 | gpm
| Fire flow requirement |  | 500 gpm for 2 hours |  | 60000 | gpd
| Unaccounted for water |  | 3.819% | of water pumped | 2370.2822 | gpd, avg
| Acceptable unaccounted for |  | 10% |  | 6189.0959 | gpd, avg
| Excess unaccounted for |  |  |  | 0 | gpd, avg
Used & Useful Analysis, in accordance with Rule 25-30.4325:
Water Treatment Plant
| Percent Used & Useful = (A + B + C - D)/E x 100%, where: |  |  |  | 100%
(System has Ground Storage)
| A = | Peak demand |  |  | 135000 | gpd
| B = | Property needed to serve five years after TY |  |  | 0 | gpd
| C = | Fire flow demand |  |  | 60000 | gpd
| D = | Excess Unaccounted for water |  |  | 0 | gpd
| E = | Firm Reliable Capacity (16 hours) |  |  | 192000 | gpd
The above used and useful factor is applicable to all source of supply, pumping and treatment accounts.
as well as the land and structures accounts.
Storage
| Percent Used & Useful = (A + B + C - D)/E x 100%, where: |  |  |  | 100%
| A = | Peak demand |  |  | 135000 | gallons
| B = | Property needed to serve five years after TY |  |  | 0 | gallons
| C = | Fire flow demand |  |  | 60000 | gallons
| D = | Excess Unaccounted for water |  |  | 0 | gallons
| E = | Firm Reliable Capacity |  |  | 30600 | gallons
The above used and useful factor is applicable to the distribution reservoir accounts.
Note: In Docket No. 20160101-WS, the Commission found the WTP & Stotage
to be 100% used and useful. There has been no change in circunstances.
It should continue to be 100% used and useful.
68

## F 6
Used and Useful Calculations |  |  |  | Florida Public Service Commission
Wastewater Treatment Plant
Company: Utilities, Inc. of Florida - Labrador |  |  |  | Schedule F-6
Docket No.: 20200139-WS |  |  |  | Page 1 of 2
Test Year Ended: December 31, 2019 |  |  |  | Preparer: Seidman, F.
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the wastewater treatment plant(s) for the historical test year
and the projected test year (if applicable).
Line
No.
Labrador (Forest Lake Estates) WWTP
1 | (A) | Used and useful flow (000):
2 |  | 3MRADF - year 2019 |  | 83446.9662
3 | (B) | Property needed for post test year period (see F-8) |  | 3354.1712
4 | (C) | Permitted capacity |  | 216000
5 | (D) | Used and useful percentage |  | 40.19%
6 | (E) | Non-used and useful percentage |  | 59.81%
7 | [F] | Used and useful percentage for rate case purposes (see note). | USE: | 100%
| NOTE: The plant serves an 894-lot MHP and a 274-lot RV park. Occupancy is subject to large seasonal variations. |  |  |  | 250320 |  | Design requiremenrts
| A plant constructed to serve full occupancy of the MHP alone at design flows of 280 gpd/ERC would require 250,000 gpd |  |  |  | 75.2045 |  | Actual gpd/ERC
capacity. However, actual flows for the whole system are closer to 75 gpd/ERC (down from 78 in 2015) in the peak 3-month period
| assuming 95% occupancy. The flow for which the plant is designed is reasonable. In addition, the system is built out. |  |  |  | 98.77% | MHP Occupancy
In Docket No. 140135-WS, and again in Docket No. 20160101-WS, the Commission rejected the argument to use 100% because
| an 11.6% parcel within the service area, owned by the developer has remained vacant may have potential for development. The Commission opted |  |  |  | 260400 |  | Design requiremenrts w/parcel
to allow 79.94%, the highest U&U allowed in a previous order, consistent with its policy to recognize the effects of conservation. The
developer has now indicated that it has plans to finally develop the parcel for 36 manufactured homes. That will use all of the parcel
and the service area will be built out. Under these circumstances, there is no longer any justification to deny finding the WWTP
100% used and useful.
All reuse related plant that can be separately identified in the accounts should be considered as 100% used & useful irrespective of
the decision regarding the WWTP.
Recap Schedules: A-6, A-10, B-14

## F 6 (2)
Used and Useful Calculations | [5 empty] | Florida Public Service Commission
Wastewater Treatment Plant
Company: Utilities, Inc. of Florida - Labrador | [5 empty] | Schedule F-6
Docket No.: 20200139-WS | [5 empty] | Page 2 of 2
Test Year Ended: December 31, 2019 | [5 empty] | Preparer: Seidman, F.
A. Infiltration allowance, excluding service laterals
Allowance @ 500
| Main dia. | Main length |  | gpd/inch-dia./mile
| inches | feet | miles | gpd | gpy
| 4 | 0 | 0 | 0
1 | 6 | 0 | 0 | 0
2 | 8 | 33989 | 6.4373 | 25749.2424
3 | 10 | 0 | 0 | 0
4 | Total | 33989 | 6.4373 | 25749.2424 | 9398473.4848
5 | Estimated Inflow @ 10% of gallons sold (L.10) |  |  |  | 2017241.8
6 | Allowable I&I |  |  |  | 11415715.2848
B. Actual Inflow & Infiltration (I&I)
7 | Wastewater treated |  |  |  | 23181200
Estimated
| Gallons Billed (not capped) to: |  |  | returned *
8 | SFR Residential WW cust. |  | 16542478 | 80% | 13233982.4
9 | All Other |  | 3629940 | 90% | 3266946
10 | Estimated flows returned |  | 20172418 |  | 16500928.4
11 | Estimated I&I (treated less returned) [L.7-L.10] |  |  |  | 6680271.6
12 | Actual I&I less allowable [L.11-L.6] |  |  |  | -4735443.6848
13 | Excess, if any [L.11-L.6, if positive] |  |  |  | 0
14 | Excess as percent of wastewater treated |  |  |  | 0%

## F 7
Used and Useful Calculations | [5 empty] | Florida Public Service Commission
Water Distribution and Wastewater Collection Systems
Company: Utilities, Inc. of Florida - Labrador | [5 empty] | Schedule F-7
Docket No.: 20200139-WS | [5 empty] | Page 1 of 1
Test Year Ended: December 31, 2019 | [5 empty] | Preparer: Seidman, F.
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the water distribution and wastewater collection systems for
the historical and the projected test year (if applicable). The capacity should be in terms of
ability to serve a designated number of connections. It should then be related to actual connected
density for historical year calculations. Explain all assumptions for projected calculations. If
the distribution and collection systems are entirely contributed or built-out, this schedule is
not required.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _
Recap Schedules: A-5,A-6,A-9,A-10,B-13,B-14
Distribution & Collection Systems
In the last three cases, Docket Nos. 110264-WS, 140135-WS and 20160101-WS, the Commission found
the distribution & collection systems to be 100% used and useful. They should continue to be so.

## F 8
Margin Reserve Calculations | [5 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida - Labrador | [5 empty] | Schedule F-8
Docket No.: 20200139-WS | [5 empty] | Page 1 of 1
Test Year Ended: December 31, 2019 | [5 empty] | Preparer: Seidman, F.
Explanation: If a margin reserve is requested, provide all calculations and analyses used to
determine the amount of margin reserve for each portion of used and useful plant.
Recap Schedules: F-5, F-6, F-7
Water Treatment & Related Facilities
PN = EG x PT x U
where:
| EG = | Equivalent annual growth in ERCs (see F-9) |  | 1.3856 | ERC/yr
| PT = | Post test year period per statute |  | 5 | yrs
| U = | Unit of measure utilized in U&U calculations |  | 119.6751 | gpd/ERC | **
| PN = | Property needed expressed in U units |  | 829.0854 | gpd
|  |  | System built out. Use: | 0 | gpd
** MDD from F-5 divided by average ERCs from F-9.
Wastewater Treatment & Related Facilities
PN = EG x PT x U
where:
| EG = | Equivalent annual growth in ERCs (see F-10) |  | 8.7345 | ERC/yr | *
| PT = | Post test year period per statute |  | 5 | yrs
| U = | Unit of measure utilized in U&U calculations |  | 76.8025 | gpd/ERC | **
| PN = | Property needed expressed in U units |  | 3354.1712 | gpd
** 3MRADF from F-6 divided by average ERCs from F-9.
Distribution & Collection Systems
The distribution & collection lines serving customers are 100 U&U. See F-7.

## F 9
Equivalent Residential Connections - Water | [7 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida - Labrador | [7 empty] | Schedule F-9
Docket No.: 20200139-WS | [7 empty] | Page 1 of 1
Test Year Ended: December 31, 2019 | [7 empty] | Preparer: Seidman, F.
Explanation: Provide the following information in order to calculate the average growth in ERCs for the last
five years, including the test year. If the utility does not have single-family residential (SFR) customers,
the largest customer class should be used as a substitute.
| (1) | (2) | (3) |  | (4) |  | (5) | (6) | (7) |  | (8) |  | (9)
|  | SFR Customers |  |  |  |  | SFR | Gallons/ | Total |  | Total |  | Annual
Line | [6 empty] | Gallons | SFR | Gallons |  | ERCs |  | % Incr.
No. | Year | Beginning | Ending |  | Average |  | Sold | (5)/(4) | Sold |  | (7)/(6) |  | in ERCs
1 | 2015 | 879 | 893 |  | 886 |  | 13571318 | 15317.5147 | 17200248 |  | 1122.9138
2 | 2016 | 893 | 883 |  | 888 |  | 13001852 | 14641.7252 | 16275632 |  | 1111.5925 |  | -1.008%
3 | 2017 | 883 | 888 |  | 885.5 |  | 12924521 | 14595.7324 | 16512611 |  | 1131.3314 |  | 1.776%
4 | 2018 | 888 | 882 |  | 885 |  | 14937445 | 16878.4689 | 19292015 |  | 1142.9956 |  | 1.031%
5 | 2019 | 882 | 900 |  | 891 |  | 16542478 | 18566.193 | 20943668 |  | 1128.054 |  | -1.307%
[9 empty] | Average Growth Through 5-Year Period (Col. 8) |  |  |  | 0.1228%
Regression Analysis per Rule 25-30.431(2)(C)
[10 empty] | X | Y
[6 empty] | Constant: |  | 1114.8724 |  | 1 | 1122.9138
[6 empty] | X Coefficient: |  | 4.1683 |  | 2 | 1111.5925
[6 empty] | R^2: |  | 0.32839 |  | 3 | 1131.3314
[10 empty] | 4 | 1142.9956
[10 empty] | 5 | 1128.054
[10 empty] | 10 | 1156.5559
[7 empty] | Five year growth |  |  |  | 28.5019 | Ercs
[7 empty] | Annual average growth |  |  |  | 5.7004 | Ercs
The Coefficient of determination - R^2 is very weak. Use simple average growth rate:
[7 empty] | Five year growth |  |  |  | 6.9278 | Ercs
[7 empty] | Annual average growth @ 0.12% |  |  |  | 1.3856 | Ercs

## F 10
Equivalent Residential Connections - Wastewater | [7 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida - Labrador | [7 empty] | Schedule F-10
Docket No.: 20200139-WS | [7 empty] | Page 1 of 1
Test Year Ended: December 31, 2019 | [7 empty] | Preparer: Seidman, F.
Explanation: Provide the following information in order to calculate the average growth in ERCs for the last
five years, including the test year. If the utility does not have single-family residential (SFR) customers,
the largest customer class should be used as a substitute.
| (1) | (2) | (3) |  | (4) |  | (5) | (6) | (7) |  | (8) |  | (9)
|  | SFR Customers |  |  |  |  | SFR | Gallons/ | Total |  | Total |  | Annual
Line | [6 empty] | Gallons | SFR | Gallons |  | ERCs |  | % Incr.
No. | Year | Beginning | Ending |  | Average |  | Sold | (5)/(4) | Sold |  | (7)/(6) |  | in ERCs
1 | 2015 | 879 | 893 |  | 886 |  | 13571318 | 15317.5147 | 16556448 |  | 1080.8834
2 | 2016 | 893 | 883 |  | 888 |  | 13001852 | 14641.7252 | 15501572 |  | 1058.7258 |  | -2.05%
3 | 2017 | 883 | 888 |  | 885.5 |  | 12924521 | 14595.7324 | 15643081 |  | 1071.7572 |  | 1.231%
4 | 2018 | 888 | 882 |  | 885 |  | 14937445 | 16878.4689 | 18412985 |  | 1090.9156 |  | 1.788%
5 | 2019 | 882 | 900 |  | 891 |  | 16542478 | 18566.193 | 20172418 |  | 1086.5134 |  | -0.4035%
[9 empty] | Average Growth Through 5-Year Period (Col. 8) |  |  |  | 0.1412%
Regression Analysis per Rule 25-30.431(2)(C)
[10 empty] | X | Y
[6 empty] | Constant: |  | 1064.7242 |  | 1 | 1080.8834
[6 empty] | X Coefficient: |  | 4.345 |  | 2 | 1058.7258
[6 empty] | R^2: |  | 0.28701 |  | 3 | 1071.7572
[10 empty] | 4 | 1090.9156
[10 empty] | 5 | 1086.5134
[10 empty] | 10 | 1108.1739
[7 empty] | Five year growth |  |  |  | 21.6605 | Ercs
[7 empty] | Annual average growth |  |  |  | 4.3321 | Ercs
The Coefficient of determination - R^2 is very weak. Use simple average growth rate:
[7 empty] | Five year growth |  |  |  | 7.6727 | Ercs
[7 empty] | Annual average growth @ 0.14% |  |  |  | 1.5345 | Ercs

## W2019 (hidden)
259/217 - Labrador
PWS ID No. 6514842
CUP No. 20 006867.006 |  | Expires: 02/17/31
FDEP Permitted Max Day Capacity of Plant - .490 mgd
Water Loss-Use'!A1
Hyper Links'!A1 |  |  |  | Total Water Used/Loss |  |  |  |  | Source Mtr Error Adj. 12/26/18 1.30% 05/20/19 -3.0% |  | Source Mtr Error Adj. 12/26/18 +24% 03/06/19 +3%
| Total | Pumped Daily Avg. | Pumped Daily Max. | Gallons Used | Gallons Loss | Total Used/ Loss | Pumped, Less Gallons Loss/ Used | Billed Consumption | Well 1 Meter Adj. % | Well 1 Pumped Meter Adj. | Well 2 Meter Adj. % | Well 2 Pumped Meter Adj. | Total Pumped Meter Adj. | Pumped, + Source Mtr Error, - Gallons Loss/ Used | Total AFW(Total Used/Loss + Billed) | AFW % plus source mtr. error | 2018 AFW %
2019-01-01 | 2.428 | 0.078323 | 0.101 | 0.068025 | 0 | 0.068025 | 2.36 | 2.2345 | 1.3% | 0.031486 | 24% | 0.00144 | 0.032926 | 2.3929 | 2.3025 | 93.56% | 91.3%
February | 2.424 | 0.086571 | 0.134 | 0.06642 | 0 | 0.06642 | 2.3576 | 2.2543 | 1.3% | 0.031486 | 24% | 0.00048 | 0.031966 | 2.3895 | 2.3207 | 94.49% | 96.93%
March | 2.784 | 0.089806 | 0.124 | 0.056195 | 0 | 0.056195 | 2.7278 | 2.5717 | 1.3% | 0.036127 | +24% +3% | 0.00099 | 0.037117 | 2.7649 | 2.6279 | 93.15% | 96.04%
April | 2.062 | 0.068733 | 0.1 | 0.020375 | 0 | 0.020375 | 2.0416 | 1.9657 | 1.3% | 0.02678 | 3% | 6e-05 | 0.02684 | 2.0685 | 1.9861 | 95.08% | 97.56%
May | 1.517 | 0.048935 | 0.076 | 0.06526 | 0 | 0.06526 | 1.4517 | 1.4945 | 1.30%&-3.0% | -0.003108 | 3% | 9e-05 | -0.003018 | 1.4487 | 1.5598 | 103% | 104.5%
June | 1.312 | 0.043733 | 0.058 | 0.06167 | 0.017 | 0.07867 | 1.2333 | 1.232 | -3% | -0.0393 | 3% | 6e-05 | -0.03924 | 1.1941 | 1.3106 | 103% | 90.31%
July | 1.312 | 0.042323 | 0.052 | 0.03476 | 0 | 0.03476 | 1.2772 | 1.1826 | -3% | -0.0393 | 3% | 6e-05 | -0.03924 | 1.238 | 1.2173 | 95.64% | 92.55%
August | 1.358 | 0.043806 | 0.072 | 0.03306 | 0 | 0.03306 | 1.3249 | 1.2464 | -3% | -0.04068 | 3% | 6e-05 | -0.04062 | 1.2843 | 1.2794 | 97.12% | 87.12%
September | 1.669 | 0.055633 | 0.135 | 0.17719 | 0.01 | 0.1872 | 1.4818 | 1.4279 | -3% | -0.05004 | 3% | 3e-05 | -0.05001 | 1.4318 | 1.6151 | 99.76% | 91.26%
October | 1.698 | 0.054774 | 0.068 | 0.05765 | 0.00438 | 0.06203 | 1.636 | 1.5991 | -3% | -0.05061 | 3% | 0.00033 | -0.05028 | 1.5857 | 1.6612 | 100.8% | 108.7%
November | 2.1025 | 0.070083 | 0.087 | 0.083238 | 0 | 0.083238 | 2.0193 | 1.8569 | -3% | -0.063045 | 3% | 3e-05 | -0.063015 | 1.9562 | 1.9401 | 95.13% | 88.65%
December | 2.2465 | 0.072468 | 0.108 | 0.086062 | 0.00198 | 0.088042 | 2.1585 | 2.151 | -3% | -0.067365 | 3% | 3e-05 | -0.067335 | 2.0911 | 2.2391 | 102.7% | 99.51%
YTD Total/Avg/Max | 22.913 | 0.062933 | 0.135 | 0.80991 | 0.03336 | 0.84327 | 22.0697 | 21.2165 |  | -0.22757 |  | 0.00366 | -0.22391 | 21.8458 | 22.0598
| 22.913 | [11 empty] | -0.22391 |  | 22.0598
| 0 | Proof to Daily Flow |  |  |  |  | Proof to Total Billed | 0 |  |  |  |  | -0.22391 |  | YTD AFW% Jan-Dec | 97.23%
Verif. W/UIWtrMn WLU wrksht & WAF Input
|  |  |  | Water Loss/Use Proof | 0
Water Loss-Use'!A1
NOTES: | [10 empty] | Well 2 | Percent | Pumped | Adjusted
[11 empty] | 03/01-03/06 | 24% | 0.004 | 0.00096
[11 empty] | 03/07-03/31 | 3% | 0.001 | 3e-05
0.00099
|  |  |  | Percentage of WL/U | [6 empty] | Well 1 | Percent | Pumped | Adjusted
|  |  |  | Jan | 2.802% | [5 empty] | 05/01-05/20 | 1.3% | 0.984 | 0.012792
|  |  |  | Feb | 2.74% | [5 empty] | 05/21-05/31 | -3% | 0.53 | -0.0159
|  |  |  | Mar | 2.018% | [8 empty] | -0.003108
|  |  |  | Apl | 0.9881%
|  |  |  | May | 4.302%
|  |  |  | June | 5.996%
|  |  |  | Jly | 2.649%
|  |  |  | Aug | 2.434%
|  |  |  | Sept | 11.22%
|  |  |  | Oct | 3.653%
|  |  |  | Nov | 3.959%
|  |  |  | Dec | 3.919%
Note on B8: Picked up from Daily Flow. Total daily flow, Column AH
Note on C8: Picked up from Daily Flow AVG, Column AI
Note on D8: Picked up from Daily Flow MAX, Column AJ
Note on E8: Click on the hyperlink at the top of this worksheet to access the Water Accountability Data Input Form for the used detail.
Note on F8: Click on the hyperlink at the top of this worksheet to access the Water Accountability Data Input Form for the loss detail.

## FLOW2019 (hidden)
259/217 - Labrador | [9 empty] | Hyper Links'!A1
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg. | Max | Proof
2019-01-01 | 0.077 | 0.064 | 0.087 | 0.101 | 0.0705 | 0.0705 | 0.06 | 0.091 | 0.076 | 0.074 | 0.101 | 0.0775 | 0.0775 | 0.065 | 0.076 | 0.08 | 0.088 | 0.098 | 0.06 | 0.06 | 0.088 | 0.088 | 0.064 | 0.089 | 0.076 | 0.076 | 0.076 | 0.066 | 0.086 | 0.076 | 0.089 | 2.428 | 0.078323 | 0.101 | 0
February | 0.099 | 0.072 | 0.072 | 0.089 | 0.088 | 0.06 | 0.093 | 0.134 | 0.0655 | 0.0655 | 0.078 | 0.076 | 0.079 | 0.088 | 0.123 | 0.078 | 0.078 | 0.087 | 0.089 | 0.089 | 0.089 | 0.11 | 0.0775 | 0.0775 | 0.101 | 0.088 | 0.077 | 0.101 |  |  |  | 2.424 | 0.086571 | 0.134 | 0
March | 0.12 | 0.087 | 0.087 | 0.077 | 0.086 | 0.101 | 0.079 | 0.124 | 0.072 | 0.072 | 0.1 | 0.071 | 0.095 | 0.088 | 0.122 | 0.0895 | 0.0895 | 0.068 | 0.098 | 0.089 | 0.1 | 0.111 | 0.078 | 0.078 | 0.077 | 0.092 | 0.073 | 0.092 | 0.12 | 0.079 | 0.079 | 2.794 | 0.089806 | 0.124 | 0
April | 0.076 | 0.077 | 0.076 | 0.1 | 0.087 | 0.071 | 0.071 | 0.076 | 0.077 | 0.066 | 0.085 | 0.088 | 0.0595 | 0.0595 | 0.065 | 0.064 | 0.065 | 0.067 | 0.093 | 0.0535 | 0.0535 | 0.065 | 0.064 | 0.064 | 0.074 | 0.063 | 0.0425 | 0.0425 | 0.064 | 0.053 |  | 2.062 | 0.068733 | 0.1 | 0
May | 0.061 | 0.054 | 0.076 | 0.0475 | 0.0475 | 0.042 | 0.056 | 0.052 | 0.041 | 0.063 | 0.0415 | 0.0415 | 0.042 | 0.049 | 0.044 | 0.045 | 0.059 | 0.042 | 0.042 | 0.041 | 0.041 | 0.052 | 0.041 | 0.052 | 0.0415 | 0.0415 | 0.041 | 0.052 | 0.063 | 0.042 | 0.063 | 1.517 | 0.048935 | 0.076 | 0
June | 0.0415 | 0.0415 | 0.048 | 0.045 | 0.048 | 0.041 | 0.051 | 0.039 | 0.039 | 0.045 | 0.038 | 0.041 | 0.041 | 0.052 | 0.0365 | 0.0365 | 0.052 | 0.042 | 0.045 | 0.058 | 0.041 | 0.042 | 0.042 | 0.041 | 0.053 | 0.041 | 0.042 | 0.051 | 0.039 | 0.039 |  | 1.312 | 0.043733 | 0.058 | 0
July | 0.046 | 0.046 | 0.052 | 0.031 | 0.041 | 0.0465 | 0.0465 | 0.039 | 0.034 | 0.041 | 0.041 | 0.052 | 0.041 | 0.041 | 0.042 | 0.041 | 0.042 | 0.041 | 0.052 | 0.041 | 0.041 | 0.042 | 0.041 | 0.042 | 0.052 | 0.041 | 0.036 | 0.036 | 0.04 | 0.043 | 0.041 | 1.312 | 0.042323 | 0.052 | 0
August | 0.031 | 0.051 | 0.036 | 0.036 | 0.042 | 0.041 | 0.041 | 0.042 | 0.052 | 0.0415 | 0.0415 | 0.03 | 0.042 | 0.035 | 0.042 | 0.055 | 0.0405 | 0.0405 | 0.032 | 0.067 | 0.03 | 0.06 | 0.057 | 0.0365 | 0.0365 | 0.051 | 0.042 | 0.041 | 0.041 | 0.052 | 0.036 | 1.322 | 0.043806 | 0.067 | 0
September | 0.036 | 0.042 | 0.052 | 0.053 | 0.063 | 0.054 | 0.0515 | 0.0515 | 0.051 | 0.042 | 0.046 | 0.041 | 0.073 | 0.057 | 0.057 | 0.135 | 0.073 | 0.053 | 0.052 | 0.063 | 0.052 | 0.052 | 0.053 | 0.052 | 0.052 | 0.041 | 0.074 | 0.047 | 0.047 | 0.053 |  | 1.669 | 0.055633 | 0.135 | 0
October | 0.052 | 0.052 | 0.064 | 0.063 | 0.052 | 0.053 | 0.046 | 0.048 | 0.049 | 0.062 | 0.068 | 0.055 | 0.056 | 0.039 | 0.055 | 0.052 | 0.063 | 0.053 | 0.047 | 0.046 | 0.042 | 0.053 | 0.063 | 0.064 | 0.052 | 0.047 | 0.047 | 0.064 | 0.052 | 0.064 | 0.064 | 1.687 | 0.054774 | 0.068 | 0
November | 0.075 | 0.056 | 0.056 | 0.07 | 0.067 | 0.059 | 0.081 | 0.051 | 0.072 | 0.072 | 0.068 | 0.072 | 0.064 | 0.075 | 0.074 | 0.065 | 0.065 | 0.076 | 0.076 | 0.087 | 0.054 | 0.087 | 0.059 | 0.059 | 0.078 | 0.087 | 0.08 | 0.072 | 0.076 | 0.0695 |  | 2.1025 | 0.070083 | 0.087 | 0
December | 0.0695 | 0.079 | 0.078 | 0.087 | 0.065 | 0.088 | 0.07 | 0.07 | 0.076 | 0.065 | 0.076 | 0.075 | 0.108 | 0.0595 | 0.0595 | 0.076 | 0.069 | 0.059 | 0.062 | 0.085 | 0.061 | 0.061 | 0.076 | 0.053 | 0.076 | 0.075 | 0.098 | 0.0595 | 0.0595 | 0.088 | 0.063 | 2.2465 | 0.072468 | 0.108 | 0
[31 empty] | Max | 2.794 |  | 0.135
[32 empty] | 22.913 | Grand Total
Peak Days
Day | 18 | 12 | 9 | 10 | 27 | 4 | 25 | 23 | 24 | 7 | 30 | 31 | 5 | 2 | 3 | 14 | 20 | 16 | 17 | 26 | 28 | 13 | 19 | 11 | 21 | 6 | 22 | 1 | 29 | 15 | 8
March | 0.068 | 0.071 | 0.072 | 0.072 | 0.073 | 0.077 | 0.077 | 0.078 | 0.078 | 0.079 | 0.079 | 0.079 | 0.086 | 0.087 | 0.087 | 0.088 | 0.089 | 0.0895 | 0.0895 | 0.092 | 0.092 | 0.095 | 0.098 | 0.1 | 0.1 | 0.101 | 0.111 | 0.12 | 0.12 | 0.122 | 0.124

## WW2019 (hidden)
2019 Labrador DMR Flow Summary
Hyperlinks!A1 |  |  | Note: Operator provides the Part B in Excel. Copy/Paste Special-Value-Transpose
[32 empty] | Total | Avg | Max | 3MADF
Spray Field FLW-01 | [31 empty] | 1.3584 | 0.04528
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1.5578 | 0.050252 |  | 0.047766
2019-01-01 | 0.0526 | 0.0567 | 0.0635 | 0.0947 | 0.043 | 0.043 | 0.0595 | 0.0601 | 0.0675 | 0.0718 | 0.1031 | 0.0606 | 0.0378 | 0.1029 | 0.0665 | 0.0651 | 0.0698 | 0.0946 | 0.05465 | 0.05465 | 0.0822 | 0.07 | 0.0617 | 0.0673 | 0.0855 | 0.0754 | 0.0754 | 0.0842 | 0.082 | 0.0687 | 0.068 | 2.1425 | 0.069113 | 0.1031 | 0.054882
February | 0.1051 | 0.06105 | 0.06105 | 0.0839 | 0.1356 | 0.0818 | 0.0974 | 0.144 | 0.0764 | 0.0764 | 0.1066 | 0.0937 | 0.0923 | 0.0952 | 0.1426 | 0.07645 | 0.07645 | 0.1111 | 0.0906 | 0.0892 | 0.0968 | 0.1239 | 0.08775 | 0.08775 | 0.0814 | 0.092 | 0.091 | 0.091 |  |  |  | 2.6485 | 0.094589 | 0.144 | 0.071318
March | 0.1222 | 0.0677 | 0.0677 | 0.0925 | 0.1074 | 0.092 | 0.0713 | 0.1255 | 0.07035 | 0.07035 | 0.0953 | 0.0859 | 0.0883 | 0.0875 | 0.1193 | 0.08265 | 0.08265 | 0.075 | 0.1006 | 0.0975 | 0.0737 | 0.1183 | 0.0637 | 0.0637 | 0.0916 | 0.0742 | 0.0832 | 0.0846 | 0.1081 | 0.0615 | 0.0615 | 2.6858 | 0.086639 | 0.1255 | 0.083447
April | 0.0791 | 0.0876 | 0.0838 | 0.0743 | 0.0884 | 0.057 | 0.057 | 0.0619 | 0.0696 | 0.0574 | 0.0566 | 0.0811 | 0.055 | 0.055 | 0.056 | 0.06 | 0.0489 | 0.0575 | 0.0825 | 0.05065 | 0.05065 | 0.0465 | 0.0435 | 0.0557 | 0.0533 | 0.0702 | 0.03385 | 0.03385 | 0.0548 | 0.0402 |  | 1.8019 | 0.060063 | 0.0884 | 0.08043
May | 0.0311 | 0.0386 | 0.0549 | 0.0321 | 0.0321 | 0.0444 | 0.0343 | 0.04 | 0.0559 | 0.0507 | 0.0322 | 0.0322 | 0.0584 | 0.0448 | 0.0322 | 0.0338 | 0.0531 | 0.024 | 0.0241 | 0.0373 | 0.0448 | 0.0182 | 0.0322 | 0.039 | 0.0303 | 0.0304 | 0.0315 | 0.0215 | 0.0289 | 0.032 | 0.0413 | 1.1363 | 0.036655 | 0.0584 | 0.061119
June | 0.0334 | 0.0334 | 0.0311 | 0.0303 | 0.0373 | 0.0325 | 0.056 | 0.0399 | 0.0399 | 0.0366 | 0.0393 | 0.0412 | 0.0367 | 0.0532 | 0.0509 | 0.0509 | 0.0497 | 0.0575 | 0.063 | 0.0483 | 0.0584 | 0.0328 | 0.0329 | 0.0384 | 0.0422 | 0.0319 | 0.0419 | 0.0429 | 0.0322 |  |  | 1.2147 | 0.041886 | 0.063 | 0.046201
July | 0.0379 | 0.0369 | 0.0381 | 0.035 | 0.0425 | 0.0556 | 0.0557 | 0.0346 | 0.043 | 0.0553 | 0.0491 | 0.0609 | 0.0413 | 0.0413 | 0.0576 | 0.0518 | 0.0485 | 0.0451 | 0.0553 | 0.0485 | 0.0484 | 0.0616 | 0.0543 | 0.0785 | 0.1092 | 0.0882 | 0.0499 | 0.05 | 0.0883 | 0.0573 | 0.074 | 1.6937 | 0.054635 | 0.1092 | 0.044392
August | 0.0639 | 0.1286 | 0.0652 | 0.0652 | 0.0777 | 0.0688 | 0.1919 | 0.0882 | 0.1054 | 0.0671 | 0.062 | 0.0954 | 0.0845 | 0.0788 | 0.1088 | 0.1243 | 0.0859 | 0.0859 | 0.0787 | 0.0757 | 0.0673 | 0.0713 | 0.0864 | 0.0534 | 0.0534 | 0.0592 | 0.0649 | 0.0632 | 0.059 | 0.0679 | 0.0591 | 2.5071 | 0.080874 | 0.1919 | 0.059132
September | 0.0591 | 0.0601 | 0.0635 | 0.0496 | 0.0536 | 0.0665 | 0.0471 | 0.0471 | 0.0474 | 0.0548 | 0.0453 | 0.0545 | 0.0698 | 0.04 | 0.04 | 0.0551 | 0.0499 | 0.0509 | 0.0478 | 0.0625 | 0.0376 | 0.0377 | 0.0451 | 0.0517 | 0.0434 | 0.0448 | 0.061 | 0.0596 | 0.0595 | 0.0461 |  | 1.5511 | 0.051703 | 0.0698 | 0.062404
October | 0.0399 | 0.0469 | 0.043 | 0.0583 | 0.0358 | 0.0359 | 0.0626 | 0.047 | 0.0541 | 0.0426 | 0.0481 | 0.044 | 0.0441 | 0.0416 | 0.0472 | 0.0471 | 0.0448 | 0.1471 | 0.0567 | 0.0565 | 0.0679 | 0.056 | 0.0629 | 0.0543 | 0.143 | 0.0639 | 0.0639 | 0.0833 | 0.056 | 0.0706 | 0.0589 | 1.824 | 0.058839 | 0.1471 | 0.063805
November | 0.0976 | 0.05555 | 0.05555 | 0.0642 | 0.0803 | 0.0557 | 0.083 | 0.086 | 0.086 | 0.0361 | 0.0609 | 0.0647 | 0.0737 | 0.0704 | 0.0793 | 0.0606 | 0.0656 | 0.0764 | 0.0785 | 0.0655 | 0.0638 | 0.0871 | 0.0626 | 0.0626 | 0.0644 | 0.0667 | 0.0647 | 0.0679 | 0.0568 | 0.0541 |  | 2.0463 | 0.06821 | 0.0976 | 0.059584
December | 0.0541 | 0.0718 | 0.0534 | 0.0798 | 0.03 | 0.0848 | 0.05245 | 0.05245 | 0.0573 | 0.058 | 0.0536 | 0.0591 | 0.0846 | 0.0465 | 0.0465 | 0.0587 | 0.0584 | 0.0628 | 0.0575 | 0.0758 | 0.0579 | 0.0579 | 0.0823 | 0.0541 | 0.0824 | 0.0621 | 0.0925 | 0.05435 | 0.05435 | 0.0735 | 0.0603 | 1.9293 | 0.062235 | 0.0925 | 0.063095
[32 empty] | 23.1812 |  |  | 0.083447
|  | 591 | 0.0591
|  | 601 | 0.0601
|  | 635 | 0.0635
|  | 496 | 0.0496
|  | 536 | 0.0536
|  | 665 | 0.0665
|  | 471 | 0.0471
|  | 471 | 0.0471
|  | 474 | 0.0474
|  | 548 | 0.0548
|  | 453 | 0.0453
|  | 545 | 0.0545
|  | 698 | 0.0698
|  | 400 | 0.04
|  | 400 | 0.04
|  | 551 | 0.0551
|  | 499 | 0.0499
|  | 509 | 0.0509
|  | 478 | 0.0478
|  | 625 | 0.0625
|  | 376 | 0.0376
|  | 377 | 0.0377
|  | 451 | 0.0451
|  | 517 | 0.0517
|  | 434 | 0.0434
|  | 448 | 0.0448
|  | 610 | 0.061
|  | 596 | 0.0596
|  | 595 | 0.0595
|  | 461 | 0.0461
0
1.5511

## Sales2019 (hidden)
Labrador, 259-217 CCB 2019
2019
Rate Schedule | Description | Rev Class | Mtr Size |  | Yr End Res Cust
259WGENS | 259 Labrador Water General Service | COML | 1" | 583650 |  |  | 46730 | 54860 | 54030 | 58380 | 48370 | 40980 | 35910 | 35540 | 41350 | 50520 | 57370 | 59610 | 583650
259WGENS | 259 Labrador Water General Service | COML | 5/8" | 336410 |  |  | 25950 | 28560 | 46500 | 67450 | 15330 | 37010 | 10580 |  | 23640 | 48780 | 8310 | 24300 | 336410
259WGENS | 259 Labrador Water General Service | COML | 6" | 3481130 |  |  | 375360 | 450580 | 412500 | 408720 | 269000 | 212800 | 185400 | 205920 | 235630 | 202880 | 211240 | 311100 | 3481130
259WRES | 259 Labrador Water Residential | RES | 5/8" | 16542478 |  |  | 1569180 | 1946491 | 1753790 | 1906127 | 1397422 | 1000320 | 1011246 | 822195 | 1004759 | 1353060 | 1256520 | 1521368 | 16542478
259WWGEN | 259 Labrador Wastewater General Service | COML | 1" | 117150 |  |  | 12990 | 11900 | 10360 | 12060 | 9110 | 6630 | 8340 | 6550 | 6930 | 7660 | 12880 | 11740 | 117150
259WWGEN | 259 Labrador Wastewater General Service | COML | 5/8" | 31660 |  |  | 2570 | 7640 | 810 | 4880 | 4500 | 5040 | 4770 |  |  |  | 110 | 1340 | 31660
259WWGEN | 259 Labrador Wastewater General Service | COML | 6" | 3481130 |  |  | 375360 | 450580 | 412500 | 408720 | 269000 | 212800 | 185400 | 205920 | 235630 | 202880 | 211240 | 311100 | 3481130
259WWRES | 259 Labrador Wastewater Residential | RES | 5/8" | 16542478 |  |  | 1569180 | 1946491 | 1753790 | 1906127 | 1397422 | 1000320 | 1011246 | 822195 | 1004759 | 1353060 | 1256520 | 1521368 | 16542478
|  |  |  | 41116086 |  |  | 3977320 | 4897102 | 4444280 | 4772464 | 3410154 | 2515900 | 2452892 | 2098320 | 2552698 | 3218840 | 3014190 | 3761926 | 41116086
Water |  |  |  | 20943668 |  |  | 2017220 | 2480491 | 2266820 | 2440677 | 1730122 | 1291110 | 1243136 | 1063655 | 1305379 | 1655240 | 1533440 | 1916378 | 20943668
Wastewater |  |  |  | 20172418 |  |  | 1960100 | 2416611 | 2177460 | 2331787 | 1680032 | 1224790 | 1209756 | 1034665 | 1247319 | 1563600 | 1480750 | 1845548 | 20172418
Total |  |  |  | 41116086 |  |  | 3977320 | 4897102 | 4444280 | 4772464 | 3410154 | 2515900 | 2452892 | 2098320 | 2552698 | 3218840 | 3014190 | 3761926 | 41116086
Water Res |  |  |  | 16542478 | 900 |  | 1569180 | 1946491 | 1753790 | 1906127 | 1397422 | 1000320 | 1011246 | 822195 | 1004759 | 1353060 | 1256520 | 1521368 | 16542478
Wastewater Res |  |  |  | 16542478 | 900 |  | 1569180 | 1946491 | 1753790 | 1906127 | 1397422 | 1000320 | 1011246 | 822195 | 1004759 | 1353060 | 1256520 | 1521368 | 16542478
2018
Rate Schedule | Description | Rev Class | Mtr Size |  | Yr End Res Cust |  | January | February | March | April | May | June | July | August | September | October | November | December | Grand Total
259WGENS | 259 Labrador Water General Service | COML | 1" | 714430 |  |  | 86760 | 69960 | 89100 | 69000 | 64250 | 53040 | 43910 | 48860 | 47890 | 39950 | 55370 | 46340 | 714430
259WGENS | 259 Labrador Water General Service | COML | 5/8" | 300860 |  |  | 26910 | 21680 | 22530 | 23860 | 23080 | 28800 | 19940 | 28940 | 24950 | 24330 | 29580 | 26260 | 300860
259WGENS | 259 Labrador Water General Service | COML | 6" | 3339280 |  |  | 346870 | 430020 | 432580 | 365010 | 170830 | 169000 | 148860 | 251880 | 202520 | 216580 | 309670 | 295460 | 3339280
259WRES | 259 Labrador Water Residential | RES | 5/8" | 14937445 |  |  | 1614180 | 1728322 | 1795720 | 1887905 | 1156633 | 854226 | 673836 | 802468 | 691210 | 759166 | 1586854 | 1386925 | 14937445
259WWGEN | 259 Labrador Wastewater General Service | COML | 1" | 112190 |  |  | 9500 | 9600 | 17430 | 12240 | 7420 | 5540 | 7620 | 9750 | 8190 | 2690 | 12890 | 9320 | 112190
259WWGEN | 259 Labrador Wastewater General Service | COML | 5/8" | 24070 |  |  | 4280 |  | 5000 |  | 2250 | 1090 | 1650 | 1370 | 7630 | 360 | 440 |  | 24070
259WWGEN | 259 Labrador Wastewater General Service | COML | 6" | 3339280 |  |  | 346870 | 430020 | 432580 | 365010 | 170830 | 169000 | 148860 | 251880 | 202520 | 216580 | 309670 | 295460 | 3339280
259WWRES | 259 Labrador Wastewater Residential | RES | 5/8" | 14937445 |  |  | 1614180 | 1728322 | 1795720 | 1887905 | 1156633 | 854226 | 673836 | 802468 | 691210 | 759166 | 1586854 | 1386925 | 14937445
|  |  |  | 37705000 |  |  | 4049550 | 4417924 | 4590660 | 4610930 | 2751926 | 2134922 | 1718512 | 2197616 | 1876120 | 2018822 | 3891328 | 3446690 | 37705000
Water |  |  |  | 19292015 |  |  | 2074720 | 2249982 | 2339930 | 2345775 | 1414793 | 1105066 | 886546 | 1132148 | 966570 | 1040026 | 1981474 | 1754985 | 19292015
Wastewater |  |  |  | 18412985 |  |  | 1974830 | 2167942 | 2250730 | 2265155 | 1337133 | 1029856 | 831966 | 1065468 | 909550 | 978796 | 1909854 | 1691705 | 18412985
Total |  |  |  | 37705000 |  |  | 4049550 | 4417924 | 4590660 | 4610930 | 2751926 | 2134922 | 1718512 | 2197616 | 1876120 | 2018822 | 3891328 | 3446690 | 37705000
Water Res |  |  |  | 14937445 | 882 |  | 1614180 | 1728322 | 1795720 | 1887905 | 1156633 | 854226 | 673836 | 802468 | 691210 | 759166 | 1586854 | 1386925 | 14937445
Wastewater Res |  |  |  | 14937445 | 882 |  | 1614180 | 1728322 | 1795720 | 1887905 | 1156633 | 854226 | 673836 | 802468 | 691210 | 759166 | 1586854 | 1386925 | 14937445
2017
Rate Schedule | Description | Rev Class | Mtr Size |  | Yr End Res Cust
259WGENS | 259 Labrador Water General Service | COML | 1" | 1007410
259WGENS | 259 Labrador Water General Service | COML | 5/8" | 50160
259WGENS | 259 Labrador Water General Service | COML | 6" | 2530520
259WRES | 259 Labrador Water Residential | RES | 5/8" | 12924521
259WWGEN | 259 Labrador Wastewater General Service | COML | 1" | 97320
259WWGEN | 259 Labrador Wastewater General Service | COML | 5/8" | 90720
259WWGEN | 259 Labrador Wastewater General Service | COML | 6" | 2530520
259WWRES | 259 Labrador Wastewater Residential | RES | 5/8" | 12924521
32155692
Water |  |  |  | 16512611
Wastewater |  |  |  | 15643081
Total |  |  |  | 32155692
Water Res |  |  |  | 12924521 | 888
Wastewater Res |  |  |  | 12924521 | 888
2016
Rate Schedule | Description | Rev Class | Mtr Size |  | Yr End Res Cust
259WGENS | 259 Labrador Water General Service | COML | 1" | 896050
259WGENS | 259 Labrador Water General Service | COML | 5/8" | 2570
259WGENS | 259 Labrador Water General Service | COML | 6" | 2375160
259WRES | 259 Labrador Water Residential | RES | 5/8" | 13001852
259WWGEN | 259 Labrador Wastewater General Service | COML | 1" | 68570
259WWGEN | 259 Labrador Wastewater General Service | COML | 5/8" | 55990
259WWGEN | 259 Labrador Wastewater General Service | COML | 6" | 2375160
259WWRES | 259 Labrador Wastewater Residential | RES | 5/8" | 13001852
31777204
Water |  |  |  | 16275632
Wastewater |  |  |  | 15501572
Total |  |  |  | 31777204
Water Res |  |  |  | 13001852 | 883
Wastewater Res |  |  |  | 13001852 | 883
2015
Rate Schedule | Description | Rev Class | Mtr Size |  | Yr End Res Cust | Begin Yr
259WGENS | 259 Labrador Water General Service | COML | 1" | 901540
259WGENS | 259 Labrador Water General Service | COML | 5/8" | 1010
259WGENS | 259 Labrador Water General Service | COML | 6" | 2726380
259WRES | 259 Labrador Water Residential | RES | 5/8" | 13571318
259WWGEN | 259 Labrador Wastewater General Service | COML | 1" | 138530
259WWGEN | 259 Labrador Wastewater General Service | COML | 5/8" | 120220
259WWGEN | 259 Labrador Wastewater General Service | COML | 6" | 2726380
259WWRES | 259 Labrador Wastewater Residential | RES | 5/8" | 13571318
33756696
Water |  |  |  | 17200248
Wastewater |  |  |  | 16556448
Total |  |  |  | 33756696
Water Res |  |  |  | 13571318 | 893 | 879
Wastewater Res |  |  |  | 13571318 | 893 | 879

## Plant (hidden)
Labrador - 2019
WATER
Production
MMADF | 160650 | gpm |  | Authorized by Water Use Permit, 6/10/2013
Annual Average | 99785 | gpm
Well 1 | 875 |  | per Annual Report 2019
Well 2 | 200
Design Capacity | 288000 | gpd | Sanitary Survey: 5/28/2019
Storage
Ground | 34000 | gallons
WASTEWATER |  |  |  | per Permit, 3/23/2015
WWTP | 0.216 | MGD, 3MRollingADF
REUSE | 0.216 | MGD, AADF