## Assumptions
General Assumptions
| Assumptions | Unit | Value
| Customers per zone | customers per zone | 350
| SCADA Controlled Devices | $ | 76000 |  | Single Circuit | Double Circuit
| Overhead reconductor | $/ft | 53.877 | 284470.56 | 392000 | 550000
| Underground reconductor | $/ft | 61.1295 | 322764 | 550000
| Transformer Upgrade | $ | 1750000 | 1500000
| Group 4 Costs | $ | 445660.9856
| Substation protection device upgrades | $ | 120000
| Feeder tie recloser | $ | 76000
| Adj. feeder midpoint recloser | $ | 76000
| Zone 1 recloser | $ | 76000
Overhead reconductor Assumptions
| Assumptions | Unit | Value
| 336 Install | $/ft | 1.39
| Conductor Removal | $/ft | 0.7
| 336 Material Cost | $/ft | 3.36
| Prep for reconductor per foot | $/ft | 5.7603
| Pole Replacement per foot | $/ft | 42.6667
| Cap bank replacement | $ | 12403
| Prep for Reconductor per pole | $ | 864.05
| Pole Replacement | $ | 6400
| Ft. per poles | ft/poles | 150
Underground reconductor Assumptions
| Assumptions | Unit | Value
| 1000 ALJCN Install/removal | $/ft | 4.8
| 6" conduit and bore | $/ft | 23.77
| ALJCN Material Cost | $/ft | 21.48
| Splices | $/ft | 1.1364
| Torsion doors per foot | $/ft | 9.9432
| Torsion doors | $ | 10500
Group 4 Assumptions
| Assumptions | Unit | Value
| Group 4 Reconductor Estimate (1 mi) | $ | 293660.9856
| 50% Mean Zone 2 load | MVA | 2.0179

## Main
Station Name | Main Feeder | Main Feeder Relay | Section_Id | Total Customers | Zone 1 Customers | Remaining Customers | Zone 2 MVA Restored | Start-up reclosers | Estimated Zone Reclosers | Adj. Station Name | Adj. Feeder | Adj Feeder Relay | End Node | Order | Region | Run Sequence | XFM OVERLOAD | Transformer Upgrade | XFM Rating | Xfmr Avail. Capacity w/ relay with FEEDER loading | Alt. Relay Load (MVA) | Alt. Relay Load (A) | Max Post Contingency Overload w/o reconductor (%) | Backbone limiting element | Max Post Contingency w/o reconductor (Amps) | Max Post Contingency Overload w/ reconductor (%) | Backbone limiting element | Max Post Contingency Overload w/ reconductor (MVA) | Max Post Contingency Overload w/ reconductor (Amps) | Backbone limiting element Rating (Amps) | Max Post Contingency Overload w/ reconductor with relay load (%) | Studied conductor upgrade (mi) | Upgrades resolve overloads? | OH Upgrades (mi) | OH Capacitor Upgrades | UG Upgrades (mi) | Cost Grouping | Start-up Recloser Cost | Substation protection device upgrades | Zone Recloser Cost | Reconductor Cost | Transformer Upgrade Cost | Group 4 Costs | Line Savers | Tripsavers | Total Estimated Cost
Fort King N | 13423 | RelayElectromechanical | 13423-10757754 | 1312 | 446 | 866 | 3.7059 | 3 | 3 | Fort King N | 13006 | RelayMicroProcessor | 13006-92949618 | 56 | DCA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 8.9048 | 0 | 0 | 89.79% | 336 ACSR | 484.8404 | 89.79% | 336 ACSR | 11.0849 | 484.8404 | 540 | 0.89785 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 228000 | 0 | 0 | 0 |  |  | 576000
Imperial Lakes | 13853 | RelayMicroProcessor | 13853-60190085 | 1429 | 323 | 1106 | 6.6029 | 3 | 4 | Mulberry W | 13010 | RelayMicroProcessor | 13010-92956889 | 17 | PCA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 22.4 | 17.0262 | 0 | 0 | 109.4% | 336 ACSR | 590.6916 | 109.4% | 336 ACSR | 13.505 | 590.6923 | 540 | 109.4% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 304000 | 0 | 0 | 445660.9856 |  |  | 977660.9856
Imperial Lakes | 13850 | RelayElectromechanical | 91845227 | 897 | 244 | 653 | 3.079 | 3 | 2 | Mulberry E | 13011 | RelayMicroProcessor | 13011-92957279 | 136 | PCA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 10.3497 | 0 | 0 | 89.57% | 2/0 AAAC | 277.6763 | 89.57% | 2/0 AAAC | 6.3485 | 277.6763 | 310 | 0.89573 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 152000 | 0 | 0 | 0 |  |  | 500000
Gibsonton | 13020 | RelayMicroProcessor | 13020-74758259 | 2991 | 417 | 2574 | 4.514 | 3 | 8 | Gibsonton | 13017 | RelayMicroProcessor | 93201249 | 1 | SHA | 1 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 2.1716 | 0 | 0 | 124.8% | 336 ACSR | 673.9818 | 124.8% | 336 ACSR | 15.4093 | 673.9818 | 540 | 124.8% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 608000 | 0 | 0 | 445660.9856 |  |  | 1281660.9856
Juneau E | 13420 | RelayMicroProcessor | 13420-74750863 | 2030 | 300 | 1730 | 5.9986 | 3 | 5 | Juneau W | 13021 | RelayMicroProcessor | 92006609 | 26 | CSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 15.7168 | 0 | 0 | 141.5% | 4/0 AAAC | 580.0328 | 107.3% | 336 ACSR | 13.2494 | 579.511 | 540 | 107.3% | 0.79962 | No | 0.79962 | 1 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 380000 | 239871.694 | 0 | 445660.9856 |  |  | 1293532.6796
Pine Lake S | 13187 | RelayMicroProcessor | 13187-74850669 | 1345 | 415 | 930 | 3.3637 | 3 | 3 | Juneau W | 13021 | RelayMicroProcessor | 60126794 | 237 | CSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 15.7168 | 0 | 0 | 122.7% | 4/0 AAAC | 503.0186 | 93.06% | 336 ACSR | 11.4893 | 502.5283 | 540 | 93.06% | 0.78295 | No | 0.78295 | 1 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 228000 | 235130.518 | 0 | 445660.9856 |  |  | 1136791.5036
Temple Terrace N | 13029 | RelayMicroProcessor | 13029-75702635 | 1252 | 289 | 963 | 3.5845 | 3 | 3 | Temple Terrace S | 13027 | RelayMicroProcessor | 13027-93576866 | 76 | CSA | 4 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 22.4 | 9.535 | 0 | 0 | 120% | 2/0 AAAC | 371.9904 | 87.39% | 6 CU | 2.4975 | 109.2393 | 125 | 0.87391 | 0.29167 | Yes | 0.29167 | 0 | 0 | Group 2:Requires conductor upgrades | 228000 | 0 | 228000 | 82970.58 | 0 | 0 |  |  | 538970.58
Temple Terrace S | 13027 | RelayMicroProcessor | 13027-75702125 | 1076 | 221 | 855 | 4.1271 | 3 | 3 | Temple Terrace N | 13029 | RelayMicroProcessor | 93543456 | 132 | CSA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 22.4 | 4.9235 | 0 | 0 | 110.4% | 6 CU | 137.9634 | 87.67% | 6 CU | 2.5055 | 109.5865 | 125 | 0.87669 | 0.15511 | Yes | 0.15511 | 1 | 0 | Group 2:Requires conductor upgrades | 228000 | 0 | 228000 | 56528.263 | 0 | 0 |  |  | 512528.263
Jan Phyl N | 13967 | RelayElectromechanical | 13967-10653046 | 1748 | 299 | 1449 | 5.5185 | 3 | 5 | Gordonville | 13030 | RelayElectromechanical | 10170208 | 107 | WHA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 12.5 | 14.9091 | 0 | 0 | 160.6% | 4/0 AAAC | 658.5678 | 122.3% | 336 ACSR | 15.1003 | 660.4673 | 540 | 122.3% | 1.008 | No | 1.008 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 240000 | 380000 | 286733.394 | 0 | 445660.9856 |  |  | 1580394.3796
South Eloise | 13473 | RelayElectromechanical | 13473-74015322 | 1275 | 253 | 1022 | 3.6938 | 3 | 3 | Gordonville | 13030 | RelayElectromechanical | 13030-60105332 | 98 | WHA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 12.5 | 14.9091 | 0 | 0 | 128.9% | 4/0 AAAC | 528.3847 | 97.5% | 336 ACSR | 12.0377 | 526.5125 | 540 | 97.5% | 1.008 | No | 1.008 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 240000 | 228000 | 286733.394 | 0 | 445660.9856 |  |  | 1428394.3796
Juneau W | 13024 | RelayMicroProcessor | 13024-74551793 | 1179 | 408 | 771 | 3.7513 | 3 | 3 | Fern St | 13043 | RelayElectromechanical | 91766556 | 75 | CSA | 1 | Adjacent XFM loaded over 100% | Fern St transformer upgrade | 28 | -0.2519 | 0 | 0 | 274.7% | 1/0 ALCN | 453.2352 | 96.75% | 336 ACSR | 11.9443 | 522.428 | 540 | 96.75% | 0.4911 | No | 0.44602 | 0 | 0.045076 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 228000 | 141429.1668 | 1750000 | 445660.9856 |  |  | 2913090.1524
Plymouth E | 13093 | RelayElectromechanical | 13093-72807040 | 1286 | 337 | 949 | 3.1319 | 3 | 3 | Fern St | 13044 | RelayMicroProcessor | 90824913 | 110 | CSA | 1 | Adjacent XFM loaded over 100% | Fern St transformer upgrade | 28 | -0.2519 | 0 | 0 | 149.4% | 2 AAAC | 298.8214 | 97.67% | 336 ACSR | 12.0588 | 527.4365 | 540 | 97.67% | 0.81553 | No | 0.81553 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 228000 | 231994.362 | 1750000 | 445660.9856 |  |  | 3003655.3476
14th St | 13046 | RelayMicroProcessor | 13046-75854083 | 1536 | 314 | 1222 | 4.3435 | 3 | 4 | Fern St | 13045 | RelayMicroProcessor | 60081140 | 146 | CSA | 1 | Adjacent XFM loaded over 100% | Fern St transformer upgrade | 28 | -0.2519 | 0 | 0 | 116.7% | 2 AAAC | 233.3005 | 87.85% | 4/0 AAAC | 8.2349 | 360.1831 | 410 | 0.8785 | 0.2553 | Yes | 0.2553 | 0 | 0 | Group 3: Requires transformer upgrade | 228000 | 0 | 304000 | 72626.196 | 1750000 | 0 |  |  | 2354626.196
Plymouth W | 13091 | RelayElectromechanical | 13091-72807193 | 1845 | 468 | 1377 | 5.3211 | 3 | 4 | 14th St | 13048 | RelayMicroProcessor | 60150515 | 72 | CSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 6.3875 | 0 | 0 | 91.8% | SGBUS | 516.8082 | 91.8% | SGBUS | 11.8158 | 516.807 | 563 | 91.8% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 304000 | 0 | 0 | 445660.9856 |  |  | 1097660.9856
Belmont | 13037 | RelayElectromechanical | 13037-74857350 | 1169 | 319 | 850 | 3.1557 | 3 | 3 | 14th St | 13049 | RelayElectromechanical | 60005689 | 174 | CSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 6.3875 | 0 | 0 | 87.4% | 4/0 AAAC | 358.3585 | 87.4% | 4/0 AAAC | 8.1932 | 358.3585 | 410 | 0.87405 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 240000 | 228000 | 0 | 0 | 0 |  |  | 696000
Temple Terrace N | 13026 | RelayMicroProcessor | 13026-75702363 | 2015 | 325 | 1690 | 4.2759 | 3 | 5 | 46th St W | 13053 | RelayMicroProcessor | 13026-93664421 | 9 | CSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 14.2741 | 0 | 0 | 94.05% | 336 ACSR | 507.8768 | 94.05% | 336 ACSR | 11.6116 | 507.8761 | 540 | 94.05% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 380000 | 0 | 0 | 445660.9856 |  |  | 1053660.9856
BAYCOURT | 13080 | RelayMicroProcessor | 13080-91896685 | 1881 | 345 | 1536 | 5.9133 | 3 | 5 | HIMES W | 13060 | RelayMicroProcessor | 13060-93275191 | 81 | WSA | 5 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 11.5592 | 0 | 0 | 164.6% | 2/0 AAAC | 510.3385 | 95.26% | 336 ACSR | 11.7603 | 514.3791 | 540 | 95.26% | 0.053977 | No | 0.053977 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 380000 | 15354.945 | 0 | 445660.9856 |  |  | 1069015.9306
MANHATTAN E | 13113 | RelayElectromechanical | 13113-60009298 | 763 | 357 | 406 | 0.6902 | 3 | 2 | HIMES W | 13060 | RelayMicroProcessor | 92820908 | 127 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 11.5592 | 0 | 0 | 88.87% | 2/0 AAAC | 275.4835 | 51.81% | 336 ACSR | 6.3964 | 279.7685 | 540 | 0.51809 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 152000 | 0 | 0 | 0 |  |  | 500000
BAYCOURT | 13082 | RelayMicroProcessor | 13082-74306606 | 1211 | 469 | 742 | 3.8282 | 3 | 3 | HIMES E | 13064 | RelayMicroProcessor | 60073795 | 221 | WSA | 2 | Adjacent XFM loaded over 100% | HIMES E transformer upgrade | 23 | -0.21288 | 0 | 0 | 105.2% | 4/0 CU | 536.5846 | 99.37% | 336 ACSR | 12.268 | 536.5839 | 540 | 99.37% | 0.04375 | No | 0.04375 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 228000 | 12445.587 | 1750000 | 445660.9856 |  |  | 2664106.5726
HIMES E | 13065 | RelayMicroProcessor | 13065-90774902 | 1684 | 239 | 1445 | 5.3521 | 3 | 5 | HIMES E | 13064 | RelayMicroProcessor | 10125956 | 232 | WSA | 5 | Adjacent XFM loaded over 100% | HIMES E transformer upgrade | 23 | -0.21288 | 0 | 0 | 116.4% | 4/0 CU | 593.5495 | 109.9% | 336 ACSR | 13.5702 | 593.5408 | 540 | 109.9% | 0.04375 | No | 0.04375 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 380000 | 12445.587 | 1750000 | 445660.9856 |  |  | 2816106.5726
HIMES E | 13064 | RelayMicroProcessor | 13064-74201365 | 2040 | 346 | 1694 | 7.3094 | 3 | 5 | HIMES E | 13065 | RelayMicroProcessor | 10125956 | 177 | WSA | 4 | Adjacent XFM loaded over 100% | HIMES E transformer upgrade | 23 | -0.21288 | 0 | 0 | 181.2% | 2/0 AAAC | 561.7475 | 110.3% | 336 ACSR | 13.6208 | 595.7574 | 540 | 110.3% | 1.0833 | No | 1.0833 | 1 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 380000 | 320579.44 | 1750000 | 445660.9856 |  |  | 3124240.4256
MACDILL E | 13605 | RelayMicroProcessor | 13605-75500856 | 715 | 337 | 378 | 1.6223 | 3 | 2 | HIMES E | 13065 | RelayMicroProcessor | 93205462 | 282 | WSA | 3 | Adjacent XFM loaded over 100% | HIMES E transformer upgrade | 23 | -0.21288 | 0 | 0 | 97.62% | 2/0 AAAC | 302.6268 | 63.27% | 336 ACSR | 7.8113 | 341.6551 | 540 | 0.63269 | 0.048674 | Yes | 0.048674 | 1 | 0 | Group 3: Requires transformer upgrade | 228000 | 0 | 152000 | 26249.389 | 1750000 | 0 |  |  | 2156249.389
HABANA N | 13137 | RelayMicroProcessor | 13137-10915965 | 786 | 345 | 441 | 2.3499 | 3 | 2 | IVY_ST | 13067 | #N/A | 90939755 | 220 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 5.0411 | 3.459 | 151.292 | 108% | 4/0 AAAC | 442.6941 | 86.64% | 4/0 CU | 10.1028 | 441.8841 | 510 | 1.1631 | 0.84356 | Yes | 0.84356 | 1 | 0 | Group 2:Requires conductor upgrades | 228000 | 120000 | 152000 | 252371.158 | 0 | 0 |  |  | 752371.158
ROME (2021) | 13522 | RelayMicroProcessor | 13522-73303821 | 2143 | 286 | 1857 | 4.7031 | 3 | 6 | IVY_ST | 13068 | #N/A | 60127453 | 15 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 5.0411 | 0 | 0 | 120.9% | 2/0 CU | 423.3204 | 80.53% | 750 CU | 9.7955 | 428.4428 | 532 | 0.80534 | 0.57348 | Yes | 0.57348 | 0 | 0 | Group 2:Requires conductor upgrades | 228000 | 120000 | 456000 | 163139.556 | 0 | 0 |  |  | 967139.556
CLEARVIEW S | 13740 | RelayMicroProcessor | 13740-72601985 | 1518 | 211 | 1307 | 5.4018 | 3 | 4 | IVY_ST | 13069 | #N/A | 91978646 | 77 | WSA | 1 | Adjacent XFM loaded over 100% | IVY_ST transformer upgrade | 28 | 5.0411 | 0 | 0 | 106.9% | 4/0 AAAC | 438.2038 | 87.52% | 2/0 AAAC | 6.2031 | 271.3155 | 310 | 0.87521 | 0.16155 | Yes | 0.16155 | 0 | 0 | Group 3: Requires transformer upgrade | 228000 | 120000 | 304000 | 45957.081 | 1750000 | 0 |  |  | 2447957.081
SILVER $ | 14274 | RelayMicroProcessor | 14274-90411696 | 1149 | 263 | 886 | 4.9378 | 3 | 3 | KEYSTONE E | 13070 | RelayMicroProcessor | 13070-92865783 | 171 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 23.1828 | 0 | 0 | 114.6% | 2 AAAC | 229.1905 | 80.98% | 336 ACSR | 9.9981 | 437.3053 | 540 | 0.80982 | 1.1074 | Yes | 1.1074 | 0 | 0 | Group 2:Requires conductor upgrades | 228000 | 0 | 228000 | 315018.819 | 0 | 0 |  |  | 771018.819
GRANADA | 13753 | RelayMicroProcessor | 13753-74006365 | 864 | 426 | 438 | 2.9845 | 3 | 2 | BAYCOURT | 13080 | RelayMicroProcessor | 60105897 | 190 | WSA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 8.827 | 0 | 0 | 115.6% | 4/0 AAAC | 473.8006 | 87.72% | 336 ACSR | 10.8297 | 473.6782 | 540 | 0.87718 | 0.34451 | Yes | 0.34451 | 0 | 0 | Group 2:Requires conductor upgrades | 228000 | 0 | 152000 | 98002.263 | 0 | 0 |  |  | 478002.263
11th Ave E | 13181 | RelayElectromechanical | 13181-75854736 | 1326 | 395 | 931 | 5.6437 | 3 | 3 | Plymouth E | 13094 | RelayMicroProcessor | 90665713 | 278 | CSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 11.566 | 0 | 0 | 143.6% | 1/0 ALCN | 236.9787 | 113.4% | 336 ACSR | 14.004 | 612.5164 | 540 | 113.4% | 0.12121 | No | 0.10265 | 0 | 0.018561 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 228000 | 35192.0295 | 0 | 445660.9856 |  |  | 1056853.0151
14th St | 13047 | RelayMicroProcessor | 13047-75853765 | 834 | 232 | 602 | 2.2718 | 3 | 2 | Plymouth E | 13094 | RelayMicroProcessor | 60650890 | 197 | CSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 11.566 | 0 | 0 | 85.94% | 336 ACSR | 464.0643 | 85.94% | 336 ACSR | 10.6098 | 464.0598 | 540 | 0.85937 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 152000 | 0 | 0 | 0 |  |  | 380000
McFarland | 13106 | RelayMicroProcessor | 13106-74853663 | 2795 | 328 | 2467 | 4.6378 | 3 | 8 | McFarland | 13104 | RelayMicroProcessor | 91648553 | 5 | CSA | 4 | Adjacent XFM loaded over 100% | McFarland transformer upgrade | 28 | 0.30825 | 0 | 0 | 91.12% | 336 ACSR | 492.0592 | 91.12% | 336 ACSR | 11.25 | 492.0592 | 540 | 91.12% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 608000 | 0 | 1750000 | 445660.9856 |  |  | 3031660.9856
McFarland | 13104 | RelayMicroProcessor | 13104-10363103 | 960 | 378 | 582 | 3.6671 | 3 | 2 | McFarland | 13106 | RelayMicroProcessor | 91648553 | 196 | CSA | 3 | Adjacent XFM loaded over 100% | McFarland transformer upgrade | 28 | 0.30825 | 0 | 0 | 221.2% | 2 AAAC | 442.3713 | 87.68% | 750 CU | 10.6644 | 466.447 | 532 | 0.87678 | 0.00018939 | Yes | 0.00018939 | 0 | 0 | Group 3: Requires transformer upgrade | 228000 | 0 | 152000 | 53.877 | 1750000 | 0 |  |  | 2130053.877
EL_PRADO | 13612 | RelayElectromechanical | 13612-90440682 | 1485 | 313 | 1172 | 3.5343 | 3 | 4 | MANHATTAN E | 13109 | RelayMicroProcessor | 90643341 | 29 | WSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 7.3341 | 0 | 0 | 74.49% | 336 ACSR | 402.2426 | 74.49% | 336 ACSR | 9.1965 | 402.2426 | 540 | 0.74489 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 304000 | 0 | 0 | 0 |  |  | 652000
EL_PRADO | 13611 | RelayElectromechanical | 13611-74308221 | 821 | 335 | 486 | 1.0208 | 3 | 2 | MANHATTAN E | 13109 | RelayMicroProcessor | 60233916 | 153 | WSA | 4 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 7.3341 | 0 | 0 | 54.51% | 336 ACSR | 294.3529 | 54.51% | 336 ACSR | 6.7298 | 294.3529 | 540 | 0.5451 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 152000 | 0 | 0 | 0 |  |  | 500000
EL_PRADO | 13613 | RelayElectromechanical | 13613-74306249 | 1140 | 319 | 821 | 3.1849 | 3 | 3 | MANHATTAN W | 13110 | RelayMicroProcessor | 10093173 | 61 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 12.4559 | 0.754 | 32.9789 | 68.48% | 1000 ALJCN | 378.6754 | 68.48% | 1000 ALJCN | 8.6577 | 378.6754 | 553 | 0.7444 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 228000 | 0 | 0 | 0 |  |  | 576000
HIMES W | 13060 | RelayMicroProcessor | 13060-74304828 | 1571 | 320 | 1251 | 4.3019 | 3 | 4 | MANHATTAN E | 13113 | RelayElectromechanical | 92820908 | 69 | WSA | 4 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 7.3341 | 0 | 0 | 141.7% | 1/0 ALCN | 233.7881 | 50.77% | 336 ACSR | 6.2685 | 274.1754 | 540 | 0.50773 | 1.6061 | Yes | 0.22879 | 0 | 1.3773 | Group 2:Requires conductor upgrades | 228000 | 120000 | 304000 | 509617.4705 | 0 | 0 |  |  | 1161617.4705
HIMES W | 13061 | RelayMicroProcessor | 13061-74305473 | 662 | 434 | 228 | 1.7821 | 3 | 1 | MANHATTAN W | 13114 | RelayMicroProcessor | 60340772 | 270 | WSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 12.4559 | 0 | 0 | 86.61% | 336 ACSR | 467.6823 | 86.61% | 336 ACSR | 10.6927 | 467.6823 | 540 | 0.86608 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 76000 | 0 | 0 | 0 |  |  | 304000
Dairy Road | 13370 | RelayMicroProcessor | 13370-75901960 | 1635 | 348 | 1287 | 5.4355 | 3 | 4 | Lake Alfred | 13117 | RelayElectromechanical | 10567855 | 128 | WHA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 5.9371 | 0 | 0 | 108.3% | 336 ACSR | 584.9048 | 108.3% | 336 ACSR | 13.3695 | 584.7633 | 540 | 108.3% | 0.080303 | No | 0.080303 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 304000 | 22843.848 | 0 | 445660.9856 |  |  | 1120504.8336
Dairy Road | 13371 | RelayMicroProcessor | 13371-75901500 | 1329 | 333 | 996 | 3.9431 | 3 | 3 | Lake Alfred | 13117 | RelayElectromechanical | 13117-92912951 | 57 | WHA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 5.9371 | 0 | 0 | 134.1% | 2 AAAC | 268.1967 | 94.82% | 336 ACSR | 11.7063 | 512.0157 | 540 | 94.82% | 1.3227 | No | 1.0746 | 0 | 0.24811 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 228000 | 385777.8025 | 0 | 445660.9856 |  |  | 1407438.7881
Lake Silver S | 13289 | RelayMicroProcessor | 13289-74013049 | 680 | 296 | 384 | 2.4652 | 3 | 2 | Lake Alfred | 13118 | RelayMicroProcessor | 10538948 | 241 | WHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 5.9371 | 0 | 0 | 102.8% | 336 ACSR | 555.2021 | 102.8% | 336 ACSR | 12.6936 | 555.2022 | 540 | 102.8% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 152000 | 0 | 0 | 445660.9856 |  |  | 825660.9856
Kirkland | 13390 | RelayMicroProcessor | 13390-74755093 | 1904 | 406 | 1498 | 4.9361 | 3 | 5 | Alexander E | 13121 | RelayMicroProcessor | 13121-92597049 | 36 | PCA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 7.0544 | 0 | 0 | 131% | 2/0 AAAC | 406.177 | 107.4% | 336 ACSR | 13.2569 | 579.8405 | 540 | 107.4% | 0.00018939 | No | 0.00018939 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 380000 | 53.877 | 0 | 445660.9856 |  |  | 1053714.8626
Twelth Ave | 13434 | RelayMicroProcessor | 13434-72704454 | 1452 | 304 | 1148 | 5.1276 | 3 | 4 | Seventy Eighth St | 13132 | RelayMicroProcessor | 92139202 | 130 | ESA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 27.6 | 15.142 | 0.4 | 17.4955 | 71.35% | 2 AAAC | 142.7001 | 71.35% | 2 AAAC | 3.2626 | 142.7001 | 200 | 0.80098 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 304000 | 0 | 0 | 0 |  |  | 532000
HABANA S | 13139 | RelayMicroProcessor | 13139-72803206 | 1535 | 240 | 1295 | 6.8154 | 3 | 4 | HABANA N | 13136 | RelayMicroProcessor | 93187353 | 192 | WSA | 1 | Adjacent XFM loaded over 100% | HABANA N transformer upgrade | 28 | 5.3071 | 0.513 | 22.4379 | 177.4% | 1/0 ALCN | 292.7282 | 81.08% | 4/0 CU | 9.4539 | 413.5022 | 510 | 0.85478 | 0.70303 | Yes | 0.54053 | 0 | 0.1625 | Group 3: Requires transformer upgrade | 228000 | 0 | 304000 | 206214.108 | 1750000 | 0 |  |  | 2488214.108
IVY_ST | 13068 | #N/A | 13068-73102799 | 1259 | 399 | 860 | 4.0017 | 3 | 3 | HABANA S | 13139 | RelayMicroProcessor | 60088185 | 251 | WSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 5.6628 | 0 | 0 | 97.63% | 336 ACSR | 527.2239 | 97.63% | 336 ACSR | 12.0538 | 527.2168 | 540 | 97.63% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 228000 | 0 | 0 | 445660.9856 |  |  | 1021660.9856
Hopewell | 13146 | RelayElectromechanical | 10629106 | 849 | 202 | 647 | 2.3915 | 3 | 2 | Hopewell | 13147 | RelayElectromechanical | 92530375 | 170 | PCA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 12.0461 | 0 | 0 | 91.44% | 336 ACSR | 493.7774 | 91.44% | 336 ACSR | 11.2893 | 493.7774 | 540 | 91.44% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 240000 | 152000 | 0 | 0 | 445660.9856 |  |  | 1065660.9856
Pinecrest | 13786 | RelayElectromechanical | 13786-76002076 | 939 | 385 | 554 | 2.1302 | 3 | 2 | Hopewell | 13148 | RelayElectromechanical | 10095566 | 138 | PCA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 12.0461 | 0 | 0 | 82.64% | 2/0 AAAC | 256.1847 | 82.64% | 2/0 AAAC | 5.8572 | 256.1847 | 310 | 0.8264 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 240000 | 152000 | 0 | 0 | 0 |  |  | 620000
Cypress Gardens | 13153 | RelayElectromechanical | 13153-74408899 | 1113 | 323 | 790 | 2.9602 | 3 | 3 | Cypress Gardens | 13151 | RelayElectromechanical | 60169548 | 165 | WHA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 3.2141 | 0 | 0 | 67.73% | 336 ACSR | 365.7627 | 67.73% | 336 ACSR | 8.3625 | 365.7627 | 540 | 0.67734 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 240000 | 228000 | 0 | 0 | 0 |  |  | 696000
Lake Ruby South | 13916 | RelayMicroProcessor | 13916-74409069 | 1796 | 305 | 1491 | 4.9486 | 3 | 5 | Cypress Gardens | 13151 | RelayElectromechanical | 60177619 | 22 | WHA | 2 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 3.2141 | 0 | 0 | 90.36% | 336 ACSR | 487.917 | 90.35% | 336 ACSR | 11.1553 | 487.9168 | 540 | 90.35% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 380000 | 0 | 0 | 445660.9856 |  |  | 1173660.9856
Cypress Gardens | 13151 | RelayElectromechanical | 13151-75154155 | 1142 | 407 | 735 | 2.2637 | 3 | 3 | Cypress Gardens | 13153 | RelayElectromechanical | 60169548 | 119 | WHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 3.2141 | 0 | 0 | 61.94% | 336 ACSR | 334.4816 | 61.94% | 336 ACSR | 7.6473 | 334.4816 | 540 | 0.61941 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 240000 | 228000 | 0 | 0 | 0 |  |  | 696000
GEORG_RD S | 13512 | RelayMicroProcessor | 13512-10238465 | 1844 | 323 | 1521 | 5.6231 | 3 | 5 | JACKSON E | 13154 | RelayElectromechanical | 60450538 | 42 | WSA | 4 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 2.3819 | 0 | 0 | 185.3% | 4/0 ALJCN | 422.4781 | 111.6% | 336 ACSR | 13.7762 | 602.5518 | 540 | 111.6% | 2.928 | No | 1.6814 | 2 | 1.2466 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 380000 | 905480.6742 | 0 | 445660.9856 |  |  | 2079141.6598
MEADOWPK E | 13671 | RelayMicroProcessor | 13671-73003926 | 1691 | 293 | 1398 | 3.9207 | 3 | 4 | JACKSON E | 13155 | RelayElectromechanical | 60156529 | 48 | WSA | 4 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 2.3819 | 0 | 0 | 93.57% | 336 ACSR | 505.2631 | 93.49% | 336 ACSR | 11.5428 | 504.8671 | 540 | 93.49% | 1.1519 | No | 0 | 0 | 1.1519 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 304000 | 371789.8955 | 0 | 445660.9856 |  |  | 1469450.8811
Fern St | 13042 | RelayMicroProcessor | 13042-74008639 | 1455 | 329 | 1126 | 3.2194 | 3 | 4 | 30th St W | 13159 | RelayElectromechanical | 13042-60253940 | 49 | CSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 8.2315 | 0 | 0 | 144.9% | 2/0 AAAC | 449.2168 | 85.22% | 336 ACSR | 10.5217 | 460.2046 | 540 | 0.85223 | 0.72311 | Yes | 0.33352 | 0 | 0.38958 | Group 2:Requires conductor upgrades | 228000 | 120000 | 304000 | 220620.872 | 0 | 0 |  |  | 872620.872
Yukon N | 13947 | RelayElectromechanical | 13947-10442064 | 1306 | 481 | 825 | 2.2894 | 3 | 3 | 30th St W | 13159 | RelayElectromechanical | 10441838 | 24 | CSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 8.2315 | 0 | 0 | 137.4% | 2/0 AAAC | 426.0492 | 81.36% | 336 ACSR | 10.0451 | 439.3599 | 540 | 0.81363 | 0.33352 | Yes | 0.33352 | 0 | 0 | Group 2:Requires conductor upgrades | 228000 | 240000 | 228000 | 94877.397 | 0 | 0 |  |  | 790877.397
CLEARVIEW S | 13737 | RelayMicroProcessor | 13737-73304635 | 849 | 303 | 546 | 2.6359 | 3 | 2 | MATANZAS N | 13161 | RelayMicroProcessor | 60019658 | 201 | WSA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 8.9482 | 0 | 0 | 85.75% | 1/0 ALCN | 141.4895 | 85.75% | 1/0 ALCN | 3.2349 | 141.4895 | 165 | 0.85751 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 152000 | 0 | 0 | 0 |  |  | 380000
LOIS W | 13072 | RelayMicroProcessor | 13072-73401335 | 751 | 352 | 399 | 3.2071 | 3 | 2 | MATANZAS S | 13162 | RelayMicroProcessor | 90390043 | 281 | WSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 5.4456 | 0 | 0 | 153.6% | 1/0 ALCN | 253.5021 | 88.2% | 336 ACSR | 10.8889 | 476.2649 | 540 | 0.88197 | 0.67822 | Yes | 0.63239 | 0 | 0.045833 | Group 2:Requires conductor upgrades | 228000 | 0 | 152000 | 194688.653 | 0 | 0 |  |  | 574688.653
GRANADA | 13754 | RelayMicroProcessor | 13754-73403295 | 1527 | 329 | 1198 | 5.4978 | 3 | 4 | MATANZAS N | 13164 | RelayMicroProcessor | 60416579 | 93 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 8.9482 | 0 | 0 | 95.04% | 4/0 CU | 484.7289 | 89.76% | 336 ACSR | 11.0824 | 484.7277 | 540 | 0.89764 | 0.1053 | Yes | 0.1053 | 0 | 0 | Group 2:Requires conductor upgrades | 228000 | 0 | 304000 | 29955.612 | 0 | 0 |  |  | 561955.612
Causeway (2018) | 14355 | RelayMicroProcessor | 14355-93058821 | 2768 | 403 | 2365 | 6.6622 | 3 | 7 | Madison S | 13169 | RelayMicroProcessor | 60322938 | 73 | ESA | 2 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 2.0961 | 0 | 0 | 158.1% | 4/0 ALJCN | 360.5277 | 121.5% | 336 ACSR | 15.0029 | 656.2047 | 540 | 121.5% | 0.99053 | No | 0.34394 | 0 | 0.64659 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 532000 | 306536.9002 | 0 | 445660.9856 |  |  | 1512197.8858
Buckhorn S | 13712 | RelayMicroProcessor | 13712-76052018 | 1136 | 351 | 785 | 3.5258 | 3 | 3 | Madison S | 13171 | RelayMicroProcessor | 10782006 | 172 | ESA | 2 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 2.0961 | 0 | 0 | 121.2% | 336 ACSR | 654.3884 | 121.2% | 336 ACSR | 14.9613 | 654.3884 | 540 | 121.2% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 228000 | 0 | 0 | 445660.9856 |  |  | 901660.9856
Madison S | 13169 | RelayMicroProcessor | 13169-75551484 | 1087 | 305 | 782 | 5.7856 | 3 | 3 | Madison N | 13173 | RelayMicroProcessor | 93386286 | 291 | ESA | 3 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 24.1613 | 0 | 0 | 123.9% | 336 ACSR | 669.1928 | 123.9% | 336 ACSR | 15.291 | 668.8082 | 540 | 123.9% | 0.97235 | No | 0 | 0 | 0.97235 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 228000 | 313839.0864 | 0 | 445660.9856 |  |  | 1215500.072
Juneau W | 13022 | RelayMicroProcessor | 13022-74550224 | 820 | 342 | 478 | 1.7623 | 3 | 2 | Pine Lake S | 13187 | RelayMicroProcessor | 60126787 | 129 | CSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 4.8969 | 0 | 0 | 79.89% | 4/0 AAAC | 327.5583 | 79.89% | 4/0 AAAC | 7.489 | 327.5583 | 410 | 0.79892 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 152000 | 0 | 0 | 0 |  |  | 380000
WOODLAND E | 13483 | RelayElectromechanical | 60117037 | 1685 | 203 | 1482 | 5.7952 | 3 | 5 | DBL_BRCH S | 13191 | RelayMicroProcessor | 91398791 | 90 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 16.5152 | 0 | 0 | 197.4% | 2 AAAC | 394.8373 | 100.2% | 336 ACSR | 12.3755 | 541.2868 | 540 | 100.2% | 0.93049 | No | 0.93049 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 380000 | 264697.701 | 0 | 445660.9856 |  |  | 1438358.6866
WSTCHASE E (69kV) | 14081 | RelayMicroProcessor | 90865516 | 1653 | 367 | 1286 | 6.9619 | 3 | 4 | DBL_BRCH S | 13192 | RelayMicroProcessor | 60645105 | 185 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 16.5152 | 0 | 0 | 182.4% | 2 AAAC | 364.719 | 67.66% | 336 ACSR | 8.3539 | 365.3897 | 540 | 0.67665 | 0.0022727 | Yes | 0.0022727 | 0 | 0 | Group 2:Requires conductor upgrades | 228000 | 0 | 304000 | 646.524 | 0 | 0 |  |  | 532646.524
WOODLAND E | 13484 | RelayElectromechanical | 13484-74552090 | 1421 | 279 | 1142 | 3.2555 | 3 | 4 | DBL_BRCH S | 13193 | RelayMicroProcessor | 60113802 | 68 | WSA | 4 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 16.5152 | 0 | 0 | 179.2% | 1/0 ALCN | 295.757 | 57.34% | 336 ACSR | 7.0788 | 309.616 | 540 | 0.57336 | 1.2042 | Yes | 0 | 0 | 1.2042 | Group 2:Requires conductor upgrades | 228000 | 120000 | 304000 | 388661.65 | 0 | 0 |  |  | 1040661.65
WOODLAND W | 13482 | RelayMicroProcessor | 13482-73204256 | 1588 | 282 | 1306 | 5.4324 | 3 | 4 | DBL_BRCH S | 13193 | RelayMicroProcessor | 60122925 | 91 | WSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 16.5152 | 0 | 0 | 192.1% | 1/0 ALCN | 316.9313 | 77.54% | 336 ACSR | 9.5733 | 418.7216 | 540 | 0.77541 | 0.84205 | Yes | 0 | 0 | 0.84205 | Group 2:Requires conductor upgrades | 228000 | 0 | 304000 | 271781.9591 | 0 | 0 |  |  | 803781.9591
WOODLAND W | 13481 | RelayElectromechanical | 60112276 | 751 | 472 | 279 | 2.281 | 3 | 1 | DBL_BRCH N | 13195 | RelayMicroProcessor | 93138885 | 195 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 11.8198 | 0 | 0 | 87.76% | 2/0 AAAC | 272.0709 | 87.76% | 2/0 AAAC | 6.2204 | 272.0709 | 310 | 0.87765 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 76000 | 0 | 0 | 0 |  |  | 424000
LOIS E | 13207 | RelayMicroProcessor | 13207-73402579 | 1102 | 287 | 815 | 4.1299 | 3 | 3 | GRAY_ST N | 13198 | RelayElectromechanical | 92190235 | 240 | WSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 8.7375 | 0 | 0 | 66.12% | 336 ACSR | 357.0281 | 66.11% | 336 ACSR | 8.1624 | 357.0113 | 540 | 0.66113 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 228000 | 0 | 0 | 0 |  |  | 576000
Yukon N | 13948 | RelayElectromechanical | 13948-75552681 | 1360 | 360 | 1000 | 5.3097 | 3 | 3 | Temple Terrace S | 13204 | RelayElectromechanical | 90297050 | 184 | CSA | 4 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 22.4 | 9.535 | 0 | 0 | 91.18% | 2 AAAC | 182.3583 | 79.63% | 336 ACSR | 9.8308 | 429.9866 | 540 | 0.79627 | 0.059091 | Yes | 0.059091 | 0 | 0 | Group 2:Requires conductor upgrades | 228000 | 240000 | 228000 | 16809.624 | 0 | 0 |  |  | 712809.624
56th St N | 13468 | RelayMicroProcessor | 13468-73207845 | 1526 | 382 | 1144 | 2.1803 | 3 | 4 | Temple Terrace S | 13205 | RelayElectromechanical | 93522354 | 27 | CSA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 22.4 | 9.535 | 0 | 0 | 72.21% | 2/0 AAAC | 223.8379 | 72.21% | 2/0 AAAC | 5.1176 | 223.8379 | 310 | 0.72206 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 304000 | 0 | 0 | 0 |  |  | 652000
MATANZAS S | 13163 | RelayMicroProcessor | 13163-74304546 | 1239 | 371 | 868 | 5.2469 | 3 | 3 | LOIS E | 13207 | RelayMicroProcessor | 10168369 | 178 | WSA | 1 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 2.9169 | 0 | 0 | 141.8% | 2/0 AAAC | 439.6907 | 101.6% | 336 ACSR | 12.5422 | 548.5806 | 540 | 101.6% | 0.74186 | No | 0.74186 | 1 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 228000 | 223439.209 | 0 | 445660.9856 |  |  | 1125100.1946
LOIS E | 13210 | RelayMicroProcessor | 13210-73501814 | 950 | 393 | 557 | 3.6804 | 3 | 2 | LOIS E | 13208 | RelayMicroProcessor | 10168825 | 210 | WSA | 1 | Adjacent XFM loaded over 100% | LOIS E transformer upgrade | 28 | 2.9169 | 0 | 0 | 139.7% | 2 AAAC | 279.4731 | 88.72% | 1/0 CU | 6.1867 | 270.5972 | 305 | 0.8872 | 0.072159 | Yes | 0.072159 | 0 | 0 | Group 3: Requires transformer upgrade | 228000 | 0 | 152000 | 20527.137 | 1750000 | 0 |  |  | 2150527.137
Orient S | 13087 | RelayElectromechanical | 13087-75556592 | 835 | 380 | 455 | 4.7464 | 3 | 2 | Fairgrounds N | 13214 | RelayElectromechanical | 60191455 | 284 | ESA | 1 | Adjacent XFM loaded over 100% | Fairgrounds N transformer upgrade | 24.5 | -5.6218 | 0 | 0 | 75.79% | 2 AAAC | 151.585 | 75.79% | 2 AAAC | 3.4657 | 151.585 | 200 | 0.75792 | 0 | No | 0 | 0 | 0 | Group 3: Requires transformer upgrade | 228000 | 240000 | 152000 | 0 | 1750000 | 0 |  |  | 2370000
Bloomingdale N | 14111 | RelayMicroProcessor | 14111-74557947 | 1279 | 347 | 932 | 4.3532 | 3 | 3 | Brandon E | 13227 | RelayMicroProcessor | 13227-93863612 | 109 | ESA | 1 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 2.0893 | 0 | 0 | 94.34% | 336 ACSR | 509.4234 | 94.34% | 336 ACSR | 11.647 | 509.4234 | 540 | 94.34% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 228000 | 0 | 0 | 445660.9856 |  |  | 901660.9856
Bloomingdale S | 13038 | RelayMicroProcessor | 13038-76102267 | 643 | 301 | 342 | 1.9913 | 3 | 1 | Brandon E | 13227 | RelayMicroProcessor | 60224476 | 273 | ESA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 2.0893 | 0 | 0 | 75.98% | 336 ACSR | 410.2761 | 75.98% | 336 ACSR | 9.3802 | 410.2761 | 540 | 0.75977 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 76000 | 0 | 0 | 0 |  |  | 304000
Lakewood N | 13457 | RelayMicroProcessor | 13457-60565278 | 881 | 330 | 551 | 3.6237 | 3 | 2 | Brandon W | 13228 | RelayMicroProcessor | 60042093 | 181 | ESA | 2 | Adjacent XFM loaded over 100% | Brandon W transformer upgrade | 24.4 | 1.1058 | 0 | 0 | 88.61% | 336 ACSR | 478.4753 | 88.61% | 336 ACSR | 10.9394 | 478.4753 | 540 | 0.88607 | 0 | No | 0 | 0 | 0 | Group 3: Requires transformer upgrade | 228000 | 0 | 152000 | 0 | 1750000 | 0 |  |  | 2130000
South Seffner E | 13129 | RelayElectromechanical | 13129-10453024 | 749 | 336 | 413 | 2.8984 | 3 | 2 | Brandon W | 13229 | RelayMicroProcessor | 60143555 | 259 | ESA | 1 | Adjacent XFM loaded over 100% | Brandon W transformer upgrade | 24.4 | 1.1058 | 0 | 0 | 82.22% | 4/0 AAAC | 337.0862 | 82.22% | 4/0 AAAC | 7.7068 | 337.0862 | 410 | 0.82216 | 0 | No | 0 | 0 | 0 | Group 3: Requires transformer upgrade | 228000 | 120000 | 152000 | 0 | 1750000 | 0 |  |  | 2250000
Bloomingdale S | 13039 | RelayMicroProcessor | 13039-73108976 | 1386 | 325 | 1061 | 4.077 | 3 | 4 | Brandon W | 13230 | RelayMicroProcessor | 10012694 | 105 | ESA | 1 | Adjacent XFM loaded over 100% | Brandon W transformer upgrade | 24.4 | 1.1058 | 3.6 | 157.4592 | 76.05% | 336 ACSR | 410.6661 | 76.05% | 1000 ALJCN | 9.3891 | 410.666 | 540 | 1.0521 | 0 | No | 0 | 0 | 0 | Group 3: Requires transformer upgrade | 228000 | 0 | 304000 | 0 | 1750000 | 0 |  |  | 2282000
Brandon E | 13226 | RelayMicroProcessor | 13226-60262999 | 1288 | 339 | 949 | 6.3877 | 3 | 3 | Brandon E | 13231 | RelayMicroProcessor | 13226-92671084 | 269 | ESA | 5 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 2.0893 | 0 | 0 | 112.7% | 336 ACSR | 608.737 | 112.7% | 336 ACSR | 13.9176 | 608.7368 | 540 | 112.7% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 228000 | 0 | 0 | 445660.9856 |  |  | 901660.9856
Saint Cloud N | 13798 | RelayMicroProcessor | 13798-73213109 | 1280 | 300 | 980 | 5.5142 | 3 | 3 | Brandon E | 13231 | RelayMicroProcessor | 60256181 | 266 | ESA | 4 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 2.0893 | 0 | 0 | 92.98% | 336 ACSR | 502.1019 | 92.98% | 336 ACSR | 11.4796 | 502.1019 | 540 | 92.98% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 228000 | 0 | 0 | 445660.9856 |  |  | 901660.9856
Sun City E | 14145 | RelayMicroProcessor | 14145-92197344 | 1735 | 311 | 1424 | 5.3921 | 3 | 5 | Caloosa N | 13233 | RelayMicroProcessor | 92212533 | 140 | SHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 17.6738 | 0 | 0 | 207.9% | 2 AAAC | 415.8023 | 77% | 336 ACSR | 9.5063 | 415.7939 | 540 | 0.76999 | 0.0030303 | Yes | 0.0030303 | 0 | 0 | Group 2:Requires conductor upgrades | 228000 | 0 | 380000 | 862.032 | 0 | 0 |  |  | 608862.032
Del Webb N | 13440 | RelayMicroProcessor | 13440-73108337 | 1695 | 308 | 1387 | 4.2372 | 3 | 4 | Caloosa N | 13235 | RelayMicroProcessor | 60578343 | 80 | SHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 17.6738 | 0 | 0 | 119.4% | 336 ACSR | 644.8077 | 119.4% | 336 ACSR | 14.7423 | 644.8077 | 540 | 119.4% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 304000 | 0 | 0 | 445660.9856 |  |  | 977660.9856
Rhodine North | 13648 | RelayMicroProcessor | 13648-76154735 | 1243 | 435 | 808 | 4.6237 | 3 | 3 | Caloosa N | 13236 | RelayMicroProcessor | 13236-92789613 | 134 | SHA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 17.6738 | 0 | 0 | 150.3% | 2/0 AAAC | 465.8623 | 94.02% | 336 ACSR | 11.6077 | 507.704 | 540 | 94.02% | 0.74886 | No | 0.74886 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 228000 | 213029.658 | 0 | 445660.9856 |  |  | 1114690.6436
Sun City E | 13303 | RelayMicroProcessor | 13303-74016450 | 2319 | 302 | 2017 | 7.1692 | 3 | 6 | Caloosa N | 13236 | RelayMicroProcessor | 13236-92471207 | 40 | SHA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 17.6738 | 0 | 0 | 195.6% | 2/0 AAAC | 606.4307 | 119.2% | 336 ACSR | 14.7149 | 643.6086 | 540 | 119.2% | 0.99318 | No | 0.99318 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 456000 | 282530.988 | 0 | 445660.9856 |  |  | 1412191.9736
Caloosa N | 13236 | RelayMicroProcessor | 13236-90040245 | 2455 | 365 | 2090 | 5.4924 | 3 | 6 | Caloosa S | 13237 | RelayMicroProcessor | 92170637 | 4 | SHA | 1 | Adjacent XFM loaded over 100% | Caloosa S transformer upgrade | 37.3 | -2.341 | 0 | 0 | 161.8% | 2/0 AAAC | 501.6552 | 137.8% | 336 ACSR | 17.0141 | 744.1725 | 540 | 137.8% | 0.22159 | No | 0.22159 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 456000 | 63036.09 | 1750000 | 445660.9856 |  |  | 2942697.0756
Ruskin W | 13003 | RelayElectromechanical | 13003-75809762 | 898 | 308 | 590 | 2.8667 | 3 | 2 | Gulf City | 13254 | RelayMicroProcessor | 13003-92219288 | 199 | SHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 12.5 | 16.034 | 0.754 | 32.9789 | 85.55% | 336 ACSR | 461.9878 | 85.55% | 336 ACSR | 10.5625 | 461.9878 | 540 | 0.91661 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 152000 | 0 | 0 | 0 |  |  | 500000
Ruskin W | 13001 | RelayElectromechanical | 13001-75809465 | 1573 | 340 | 1233 | 5.4622 | 3 | 4 | Gulf City | 13254 | RelayMicroProcessor | 60179352 | 117 | SHA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 12.5 | 16.034 | 0.754 | 32.9789 | 153.3% | 2 AAAC | 306.6069 | 99.25% | 336 ACSR | 12.2528 | 535.9231 | 540 | 105.4% | 0.00018939 | No | 0.00018939 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 304000 | 53.877 | 0 | 445660.9856 |  |  | 1097714.8626
Ruskin E | 13817 | RelayElectromechanical | 13817-90197115 | 1921 | 300 | 1621 | 4.6731 | 3 | 5 | Gulf City | 13256 | RelayMicroProcessor | 13256-93118770 | 14 | SHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 12.5 | 16.034 | 0 | 0 | 81.11% | 336 ACSR | 438.0139 | 81.11% | 336 ACSR | 10.0143 | 438.0138 | 540 | 0.81114 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 380000 | 0 | 0 | 0 |  |  | 728000
Hampton N. | 13657 | RelayMicroProcessor | 13657-75257209 | 866 | 295 | 571 | 2.1704 | 3 | 2 | JD Page (Compark) | 13268 | RelayMicroProcessor | 10070821 | 228 | PCA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 13.0503 | 0 | 0 | 80.37% | 2/0 AAAC | 249.1476 | 80.37% | 2/0 AAAC | 5.6963 | 249.1476 | 310 | 0.8037 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 152000 | 0 | 0 | 0 |  |  | 380000
Jan Phyl N | 13968 | RelayElectromechanical | 13968-74012600 | 1182 | 277 | 905 | 2.6857 | 3 | 3 | Lake Silver S | 13290 | RelayMicroProcessor | 10565962 | 38 | WHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 14.68 | 0 | 0 | 56.6% | 4/0 AAAC | 232.073 | 56.6% | 4/0 AAAC | 5.3059 | 232.073 | 410 | 0.56603 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 228000 | 0 | 0 | 0 |  |  | 576000
E Winter Haven W | 13311 | RelayMicroProcessor | 13311-75353193 | 928 | 300 | 628 | 2.9081 | 3 | 2 | Lake Silver N | 13292 | RelayElectromechanical | 92284855 | 155 | WHA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 14.193 | 0 | 0 | 51.76% | 336 ACSR | 279.4925 | 51.76% | 336 ACSR | 6.3901 | 279.4925 | 540 | 0.51758 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 152000 | 0 | 0 | 0 |  |  | 500000
Lake Silver N | 13292 | RelayElectromechanical | 13292-74014066 | 605 | 358 | 247 | 1.3231 | 3 | 1 | Lake Silver N | 13293 | RelayMicroProcessor | 91099875 | 263 | WHA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 14.193 | 0 | 0 | 47.79% | 336 ACSR | 258.0527 | 47.79% | 336 ACSR | 5.8999 | 258.0527 | 540 | 0.47788 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 76000 | 0 | 0 | 0 |  |  | 424000
Sun City W | 13302 | RelayMicroProcessor | 13302-73107742 | 1777 | 300 | 1477 | 5.1922 | 3 | 5 | Sun City W | 13304 | RelayMicroProcessor | 60198849 | 58 | SHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 13.0395 | 0 | 0 | 119% | 336 ACSR | 642.8597 | 119% | 336 ACSR | 14.6977 | 642.8597 | 540 | 119% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 380000 | 0 | 0 | 445660.9856 |  |  | 1053660.9856
Jan Phyl S | 13297 | RelayElectromechanical | 13297-10560854 | 1479 | 475 | 1004 | 3.7002 | 3 | 3 | E Winter Haven W | 13309 | RelayMicroProcessor | 10560633 | 44 | WHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 9.6161 | 0 | 0 | 78.56% | 4/0 AAAC | 322.1021 | 78.56% | 4/0 AAAC | 7.3642 | 322.1021 | 410 | 0.78561 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 228000 | 0 | 0 | 0 |  |  | 576000
Lake Region | 13444 | RelayMicroProcessor | 13444-75953176 | 688 | 470 | 218 | 1.4615 | 3 | 1 | E Winter Haven W | 13311 | RelayMicroProcessor | 90418435 | 213 | WHA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 9.6161 | 0 | 0 | 45.21% | 336 ACSR | 244.1217 | 45.21% | 336 ACSR | 5.5814 | 244.1217 | 540 | 0.45208 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 76000 | 0 | 0 | 0 |  |  | 304000
E Winter Haven E | 13312 | RelayMicroProcessor | 13312-75353545 | 982 | 335 | 647 | 3.8562 | 3 | 2 | E Winter Haven E | 13314 | RelayMicroProcessor | 10567143 | 261 | WHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 8.1 | 0 | 0 | 133.8% | 2 AAAC | 267.5426 | 62.72% | 336 ACSR | 7.744 | 338.7102 | 540 | 0.62724 | 0.65303 | Yes | 0.65303 | 0 | 0 | Group 2:Requires conductor upgrades | 228000 | 0 | 152000 | 185767.896 | 0 | 0 |  |  | 565767.896
GEORG_RD S | 13511 | RelayMicroProcessor | 13511-74201063 | 795 | 309 | 486 | 3.8912 | 3 | 2 | SKYWAY N | 13322 | RelayMicroProcessor | 92476738 | 279 | WSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 10.2266 | 1.4 | 61.2341 | 105.9% | 1/0 ALCN | 174.8052 | 88.96% | 1/0 ALCN | 3.3561 | 146.7911 | 165 | 1.2608 | 0.042803 | Yes | 0 | 0 | 0.042803 | Group 2:Requires conductor upgrades | 228000 | 0 | 152000 | 13815.2773 | 0 | 0 |  |  | 393815.2773
SKYWAY N | 13270 | RelayMicroProcessor | 13270-10196197 | 559 | 364 | 195 | 1.0433 | 3 | 1 | SKYWAY N | 13323 | RelayMicroProcessor | 93139886 | 248 | WSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 10.2266 | 0 | 0 | 31.66% | 336 ACSR | 170.9407 | 31.66% | 336 ACSR | 3.9082 | 170.9408 | 540 | 0.31656 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 76000 | 0 | 0 | 0 |  |  | 304000
Twelth Ave | 13435 | RelayMicroProcessor | 13435-74316373 | 862 | 361 | 501 | 3.9515 | 3 | 2 | Port Sutton S. | 13324 | RelayMicroProcessor | 60146731 | 223 | ESA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 24.3419 | 0 | 0 | 57.85% | 1000 ALJCN | 319.9084 | 57.85% | 1000 ALJCN | 7.3141 | 319.9084 | 553 | 0.5785 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 152000 | 0 | 0 | 0 |  |  | 380000
Dade City S | 13328 | RelayMicroProcessor | 13328-75806900 | 643 | 325 | 318 | 1.6272 | 3 | 1 | Dade City N | 13329 | RelayMicroProcessor | 60208666 | 256 | DCA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 11.6506 | 0 | 0 | 60.37% | 2 AAAC | 120.7449 | 60.37% | 2 AAAC | 2.7606 | 120.7449 | 200 | 0.60372 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 76000 | 0 | 0 | 0 |  |  | 304000
Fort King S | 13005 | RelayElectromechanical | 13005-73701901 | 723 | 310 | 413 | 2.1709 | 3 | 2 | Dade City N | 13329 | RelayMicroProcessor | 60061758 | 224 | DCA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 11.6506 | 0 | 0 | 63.73% | 2/0 AAAC | 197.564 | 63.73% | 2/0 AAAC | 4.5169 | 197.564 | 310 | 0.6373 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 152000 | 0 | 0 | 0 |  |  | 500000
Blanton | 13815 | RelayMicroProcessor | 13815-74753242 | 727 | 307 | 420 | 2.1887 | 3 | 2 | Dade City N | 13330 | RelayMicroProcessor | 10745763 | 194 | DCA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 11.6506 | 0 | 0 | 74.28% | 336 ACSR | 401.0916 | 74.27% | 336 ACSR | 9.1698 | 401.0735 | 540 | 0.74273 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 152000 | 0 | 0 | 0 |  |  | 380000
Blanton | 13813 | RelayMicroProcessor | 13813-75654066 | 975 | 301 | 674 | 2.4983 | 3 | 2 | Dade City N | 13331 | RelayMicroProcessor | 13331-92635783 | 272 | DCA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 11.6506 | 0 | 0 | 86.82% | 2/0 AAAC | 269.1405 | 86.82% | 2/0 AAAC | 6.1534 | 269.1406 | 310 | 0.8682 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 152000 | 0 | 0 | 0 |  |  | 380000
WATERS E | 13337 | RelayMicroProcessor | 13337-74403994 | 2410 | 298 | 2112 | 6.1992 | 3 | 7 | WATERS W | 13333 | RelayMicroProcessor | 92580533 | 28 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 6.308 | 0 | 0 | 89.9% | 750 CU | 478.2697 | 89.9% | 750 CU | 10.9347 | 478.2697 | 532 | 0.899 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 532000 | 0 | 0 | 0 |  |  | 760000
COOLIDGE W | 13530 | RelayElectromechanical | 13530-74005167 | 855 | 322 | 533 | 2.5422 | 3 | 2 | WATERS W | 13338 | RelayMicroProcessor | 60092106 | 163 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 6.308 | 0 | 0 | 60.51% | 750 CU | 321.8928 | 60.51% | 750 CU | 7.3595 | 321.8928 | 532 | 0.60506 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 152000 | 0 | 0 | 0 |  |  | 500000
East Bay N | 13341 | RelayMicroProcessor | 13341-75603904 | 820 | 401 | 419 | 1.5888 | 3 | 2 | East Bay N | 13346 | RelayMicroProcessor | 92922322 | 238 | SHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 6.9591 | 0 | 0 | 100.2% | SGBUS | 563.9363 | 100.2% | SGBUS | 12.8933 | 563.9363 | 563 | 100.2% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 152000 | 0 | 0 | 445660.9856 |  |  | 825660.9856
27th St S | 13354 | RelayElectromechanical | 13354-10582604 | 1838 | 297 | 1541 | 4.3202 | 3 | 5 | 27th St S | 13349 | RelayElectromechanical | 60140708 | 46 | CSA | 1 | Adjacent XFM loaded over 100% | 27th St S transformer upgrade | 28 | 2.4253 | 3.1 | 135.5898 | 183.6% | 2 AAAC | 367.2646 | 67.99% | 336 ACSR | 8.3946 | 367.1696 | 540 | 0.93104 | 0.02197 | Yes | 0.02197 | 0 | 0 | Group 3: Requires transformer upgrade | 228000 | 240000 | 380000 | 6249.732 | 1750000 | 0 |  |  | 2604249.732
27th St S | 13348 | RelayElectromechanical | 13348-10383634 | 2699 | 379 | 2320 | 5.3834 | 3 | 7 | 27th St N | 13351 | RelayMicroProcessor | 91533183 | 8 | CSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 14.2147 | 0 | 0 | 229.4% | 2 AAAC | 458.875 | 92.96% | 336 ACSR | 11.4768 | 501.9814 | 540 | 92.96% | 0.21023 | No | 0.21023 | 1 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 532000 | 72206.47 | 0 | 445660.9856 |  |  | 1397867.4556
HYDE_PRK N | 13141 | RelayMicroProcessor | 13141-10147483 | 1199 | 205 | 994 | 5.2316 | 3 | 3 | HYDE_PRK S | 13358 | RelayMicroProcessor | 10147409 | 104 | WSA | 1 | Adjacent XFM loaded over 100% | HYDE_PRK S transformer upgrade | 23 | -0.53099 | 1.5 | 65.608 | 177.5% | 2 AAAC | 354.9377 | 113.8% | 1000 ALJCN | 14.3929 | 629.524 | 553 | 125.7% | 0.019129 | No | 0.019129 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 228000 | 5441.577 | 1750000 | 445660.9856 |  |  | 2657102.5626
HYDE_PRK N | 13143 | RelayMicroProcessor | 13143-75052560 | 1677 | 310 | 1367 | 6.4013 | 3 | 4 | HYDE_PRK S | 13359 | RelayMicroProcessor | 60087098 | 205 | WSA | 1 | Adjacent XFM loaded over 100% | HYDE_PRK S transformer upgrade | 23 | -0.53099 | 0 | 0 | 99.86% | 500 CU | 478.3493 | 98.55% | 336 ACSR | 12.1665 | 532.1453 | 540 | 98.55% | 1.2477 | No | 0.030492 | 0 | 1.2172 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 304000 | 401553.7856 | 1750000 | 445660.9856 |  |  | 3129214.7712
46th St W | 13051 | RelayMicroProcessor | 13051-75153193 | 1125 | 338 | 787 | 2.1776 | 3 | 3 | USF W | 13365 | RelayMicroProcessor | 60291596 | 71 | CSA | 1 | Adjacent XFM loaded over 100% | USF W transformer upgrade | 37.3 | -7.0135 | 0 | 0 | 90.15% | 1/0 ALCN | 148.7552 | 81.88% | 336 ACSR | 10.1086 | 442.1347 | 540 | 81.88% | 0.09697 | Yes | 0 | 0 | 0.09697 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 228000 | 31298.3273 | 1750000 | 445660.9856 |  |  | 2682959.3129
Lake Alfred | 13117 | RelayElectromechanical | 13117-73210718 | 2089 | 310 | 1779 | 5.6895 | 3 | 6 | Dairy Road | 13371 | RelayMicroProcessor | 13117-92912951 | 19 | WHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 9.0664 | 0 | 0 | 147.8% | 2 AAAC | 295.5981 | 89.81% | 336 ACSR | 11.0876 | 484.9562 | 540 | 0.89807 | 1.3227 | Yes | 1.0746 | 1 | 0.24811 | Group 2:Requires conductor upgrades | 228000 | 120000 | 456000 | 398180.8025 | 0 | 0 |  |  | 1202180.8025
Lake Silver N | 13291 | RelayElectromechanical | 13291-74012986 | 819 | 308 | 511 | 2.5283 | 3 | 2 | Dairy Road | 13373 | RelayElectromechanical | 13291-92483076 | 253 | WHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 9.0664 | 0 | 0 | 99.11% | 336 ACSR | 535.2172 | 99.12% | 336 ACSR | 12.2374 | 535.2492 | 540 | 99.12% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 240000 | 152000 | 0 | 0 | 445660.9856 |  |  | 1065660.9856
Lake Silver S | 13290 | RelayMicroProcessor | 13290-74012897 | 1129 | 375 | 754 | 1.9614 | 3 | 3 | Dairy Road | 13373 | RelayElectromechanical | 10025127 | 59 | WHA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 9.0664 | 0 | 0 | 118.2% | 2 AAAC | 236.407 | 94.69% | 336 ACSR | 11.6902 | 511.3121 | 540 | 94.69% | 0.038258 | No | 0.038258 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 228000 | 10883.154 | 0 | 445660.9856 |  |  | 1032544.1396
HYDE_PRK N | 13142 | RelayMicroProcessor | 13142-74006738 | 1864 | 302 | 1562 | 5.0244 | 3 | 5 | PLANT_AV E | 13377 | RelayMicroProcessor | 60301264 | 62 | WSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 22.4139 | 0 | 0 | 95.62% | 500 CU | 458.035 | 86.1% | 750 CU | 10.472 | 458.0298 | 532 | 0.86096 | 0.023485 | Yes | 0 | 0 | 0.023485 | Group 2:Requires conductor upgrades | 228000 | 0 | 380000 | 7580.0636 | 0 | 0 |  |  | 615580.0636
HYDE_PRK S | 13359 | RelayMicroProcessor | 13359-75850174 | 992 | 324 | 668 | 4.9656 | 3 | 2 | PLANT_AV E | 13377 | RelayMicroProcessor | 90537993 | 226 | WSA | 4 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 22.4139 | 0 | 0 | 144.1% | 1/0 ALCN | 237.7696 | 88.21% | 750 CU | 10.7288 | 469.2636 | 532 | 0.88207 | 4.927 | Yes | 1.1011 | 1 | 3.8259 | Group 2:Requires conductor upgrades | 228000 | 0 | 152000 | 1560491.1998 | 0 | 0 |  |  | 1940491.1998
Gallagher N | 13723 | RelayMicroProcessor | 13723-75156385 | 707 | 315 | 392 | 2.0144 | 3 | 2 | Kirkland | 13388 | RelayMicroProcessor | 91705066 | 245 | PCA | 1 | Adjacent XFM loaded over 100% | Kirkland transformer upgrade | 28 | 1.8492 | 0 | 0 | 69.16% | 336 ACSR | 373.4846 | 69.16% | 336 ACSR | 8.539 | 373.4846 | 540 | 0.69164 | 0 | No | 0 | 0 | 0 | Group 3: Requires transformer upgrade | 228000 | 0 | 152000 | 0 | 1750000 | 0 |  |  | 2130000
Gallagher N | 13724 | RelayElectromechanical | 10671360 | 1517 | 225 | 1292 | 5.664 | 3 | 4 | Kirkland | 13389 | RelayMicroProcessor | 10087627 | 106 | PCA | 3 | Adjacent XFM loaded over 100% | Kirkland transformer upgrade | 28 | 1.8492 | 0 | 0 | 139.2% | 2 AAAC | 278.38 | 92.93% | 336 ACSR | 11.4732 | 501.8226 | 540 | 92.93% | 0.71439 | No | 0.026136 | 0 | 0.68826 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 304000 | 229579.7942 | 1750000 | 445660.9856 |  |  | 3077240.7798
Wilson | 13241 | RelayMicroProcessor | 10633843 | 1734 | 493 | 1241 | 4.8953 | 3 | 4 | Kirkland | 13390 | RelayMicroProcessor | 13241-92609999 | 87 | PCA | 1 | Adjacent XFM loaded over 100% | Kirkland transformer upgrade | 28 | 1.8492 | 0 | 0 | 97.22% | 336 ACSR | 524.9863 | 97.22% | 336 ACSR | 12.0028 | 524.9863 | 540 | 97.22% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 304000 | 0 | 1750000 | 445660.9856 |  |  | 2727660.9856
Alexander E | 13123 | RelayMicroProcessor | 13123-75254726 | 1197 | 349 | 848 | 3.681 | 3 | 3 | Plant City | 13414 | RelayMicroProcessor | 60296435 | 82 | PCA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 3.7377 | 0 | 0 | 74.67% | 336 ACSR | 403.2361 | 74.67% | 336 ACSR | 9.2192 | 403.2361 | 540 | 0.74673 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 228000 | 0 | 0 | 0 |  |  | 456000
Wilson | 13243 | RelayMicroProcessor | 13243-10792272 | 1464 | 327 | 1137 | 5.6033 | 3 | 4 | Plant City | 13414 | RelayMicroProcessor | 60211020 | 179 | PCA | 2 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 3.7377 | 0 | 0 | 97.59% | 336 ACSR | 526.9982 | 97.58% | 336 ACSR | 12.0478 | 526.9542 | 540 | 97.58% | 0.057765 | No | 0.027841 | 0 | 0.029924 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 304000 | 17578.3872 | 0 | 445660.9856 |  |  | 995239.3728
Seneca N | 13592 | RelayMicroProcessor | 13592-91836675 | 1495 | 295 | 1200 | 4.42 | 3 | 4 | Juneau E | 13417 | RelayMicroProcessor | 92761925 | 31 | CSA | 5 | Adjacent XFM loaded over 100% | Juneau E transformer upgrade | 28 | 2.3088 | 0 | 0 | 146.1% | 1/0 ALCN | 241.0258 | 81.32% | 4/0 ALJCN | 4.2393 | 185.4197 | 228 | 0.81324 | 0.56951 | Yes | 0.089205 | 0 | 0.4803 | Group 3: Requires transformer upgrade | 228000 | 0 | 304000 | 180400.5943 | 1750000 | 0 |  |  | 2462400.5943
Yukon S | 13101 | RelayElectromechanical | 13101-75804689 | 701 | 345 | 356 | 2.1153 | 3 | 2 | Juneau E | 13417 | RelayMicroProcessor | 90735357 | 276 | CSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 2.3088 | 0 | 0 | 60.42% | 2/0 AAAC | 187.2902 | 55.85% | 336 ACSR | 6.8957 | 301.6087 | 540 | 0.55853 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 152000 | 0 | 0 | 0 |  |  | 500000
Juneau W | 13023 | RelayMicroProcessor | 13023-72801788 | 1551 | 213 | 1338 | 5.0684 | 3 | 4 | Juneau E | 13419 | RelayMicroProcessor | 60001352 | 222 | CSA | 1 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 2.3088 | 0 | 0 | 194.4% | 2 AAAC | 388.7909 | 109% | 336 ACSR | 13.4544 | 588.4773 | 540 | 109% | 0.021212 | No | 0.021212 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 304000 | 6034.224 | 0 | 445660.9856 |  |  | 983695.2096
Fort King N | 13006 | RelayMicroProcessor | 13006-93038852 | 1818 | 230 | 1588 | 5.9436 | 3 | 5 | Fort King N | 13423 | RelayElectromechanical | 90829560 | 63 | DCA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 8.9048 | 0 | 0 | 89.58% | 2/0 AAAC | 277.6883 | 89.58% | 2/0 AAAC | 6.3488 | 277.6883 | 310 | 0.89577 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 380000 | 0 | 0 | 0 |  |  | 728000
ROCKY_CR N | 13573 | RelayMicroProcessor | 13573-73204074 | 1062 | 430 | 632 | 3.492 | 3 | 2 | ROCKY_CR S | 13425 | RelayMicroProcessor | 93040128 | 126 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 4.8786 | 0 | 0 | 87.72% | 336 ACSR | 473.7099 | 87.72% | 336 ACSR | 10.8305 | 473.7099 | 540 | 0.87724 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 152000 | 0 | 0 | 0 |  |  | 380000
JACKSON E | 13157 | RelayElectromechanical | 13157-90547799 | 697 | 322 | 375 | 2.1617 | 3 | 2 | ROCKY_CR S | 13427 | RelayMicroProcessor | 91431197 | 292 | WSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 4.8786 | 0 | 0 | 83.93% | 4/0 ALJCN | 191.3556 | 83.93% | 4/0 ALJCN | 4.375 | 191.3556 | 228 | 0.83928 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 152000 | 0 | 0 | 0 |  |  | 500000
JACKSON W | 13491 | RelayElectromechanical | 13491-73003716 | 1802 | 388 | 1414 | 4.6261 | 3 | 5 | ROCKY_CR S | 13428 | RelayMicroProcessor | 60160806 | 25 | WSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 4.8786 | 0 | 0 | 91.98% | 336 ACSR | 496.674 | 91.98% | 336 ACSR | 11.3555 | 496.674 | 540 | 91.98% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 380000 | 0 | 0 | 445660.9856 |  |  | 1173660.9856
PATSN_RD W | 13860 | RelayElectromechanical | 13860-10307596 | 1031 | 303 | 728 | 4.3946 | 3 | 3 | ROCKY_CR S | 13428 | RelayMicroProcessor | 10213741 | 180 | WSA | 4 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 4.8786 | 0 | 0 | 84.73% | 336 ACSR | 457.5621 | 84.73% | 336 ACSR | 10.4613 | 457.5621 | 540 | 0.84734 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 228000 | 0 | 0 | 0 |  |  | 576000
PATSN_RD W | 13863 | RelayElectromechanical | 13863-60171333 | 740 | 311 | 429 | 2.8018 | 3 | 2 | ROCKY_CR S | 13428 | RelayMicroProcessor | 60113182 | 249 | WSA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 4.8786 | 0 | 0 | 66.47% | 336 ACSR | 358.9473 | 66.47% | 336 ACSR | 8.2066 | 358.9473 | 540 | 0.66472 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 152000 | 0 | 0 | 0 |  |  | 500000
Del Webb S | 13489 | RelayMicroProcessor | 13489-92224037 | 533 | 293 | 240 | 0.8437 | 3 | 1 | Del Webb N | 13438 | RelayMicroProcessor | 13438-92594929 | 280 | SHA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 3.9938 | 0 | 0 | 85.02% | 336 ACSR | 459.0969 | 85.02% | 336 ACSR | 10.4964 | 459.0972 | 540 | 0.85018 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 76000 | 0 | 0 | 0 |  |  | 304000
Sun City E | 14144 | RelayMicroProcessor | 14144-92327213 | 1855 | 369 | 1486 | 5.1685 | 3 | 5 | Del Webb N | 13439 | RelayMicroProcessor | 13439-92958678 | 30 | SHA | 1 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 3.9938 | 0 | 0 | 102.9% | 336 ACSR | 555.5612 | 102.9% | 336 ACSR | 12.7018 | 555.5612 | 540 | 102.9% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 380000 | 0 | 0 | 445660.9856 |  |  | 1053660.9856
Lake Silver N | 13293 | RelayMicroProcessor | 13293-74013683 | 1762 | 337 | 1425 | 3.681 | 3 | 5 | Lake Region | 13442 | RelayMicroProcessor | 10563875 | 13 | WHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 7.5787 | 0 | 0 | 110.7% | 336 ACSR | 597.9098 | 110.7% | 336 ACSR | 13.6637 | 597.6325 | 540 | 110.7% | 0.6017 | No | 0.6017 | 1 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 380000 | 183570.229 | 0 | 445660.9856 |  |  | 1237231.2146
Cypress Gardens | 13152 | RelayMicroProcessor | 13152-74407902 | 1042 | 311 | 731 | 3.4134 | 3 | 3 | Lake Region | 13444 | RelayMicroProcessor | 60312019 | 149 | WHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 7.5787 | 0 | 0 | 118.5% | 1/0 ALCN | 195.5736 | 86.58% | 4/0 ALJCN | 4.5134 | 197.4097 | 228 | 0.86583 | 0.48182 | Yes | 0 | 0 | 0.48182 | Group 2:Requires conductor upgrades | 228000 | 0 | 228000 | 155513.5636 | 0 | 0 |  |  | 611513.5636
CYPRESS E | 13448 | RelayMicroProcessor | 13448-90162826 | 602 | 383 | 219 | 0.5298 | 3 | 1 | CYPRESS E | 13449 | RelayMicroProcessor | 60576788 | 285 | WSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 19.645 | 0 | 0 | 44.08% | 2 AAAC | 88.163 | 44.08% | 2 AAAC | 2.0157 | 88.163 | 200 | 0.44082 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 76000 | 0 | 0 | 0 |  |  | 304000
Lakewood S | 13456 | RelayMicroProcessor | 13456-75358745 | 1014 | 247 | 767 | 2.5194 | 3 | 3 | Lakewood S | 13454 | RelayMicroProcessor | 60532060 | 162 | ESA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 2.7363 | 0 | 0 | 87.14% | 336 ACSR | 470.5477 | 87.14% | 336 ACSR | 10.7582 | 470.5477 | 540 | 0.87138 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 228000 | 0 | 0 | 0 |  |  | 456000
Lakewood S | 13455 | RelayMicroProcessor | 13455-90276889 | 1048 | 301 | 747 | 2.1966 | 3 | 3 | Lakewood N | 13457 | RelayMicroProcessor | 60304863 | 94 | ESA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 16.7964 | 0 | 0 | 50.84% | 1000 ALJCN | 281.1553 | 50.84% | 1000 ALJCN | 6.4281 | 281.1553 | 553 | 0.50842 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 228000 | 0 | 0 | 0 |  |  | 456000
Clarkwild West | 13458 | RelayMicroProcessor | 13458-90175823 | 682 | 328 | 354 | 1.8239 | 3 | 2 | Clarkwild West | 13460 | RelayMicroProcessor | 93054637 | 262 | ESA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 3.2987 | 0 | 0 | 112.9% | 2/0 AAAC | 349.8615 | 82.56% | 2 AAAC | 3.7752 | 165.1234 | 200 | 0.82562 | 0.46193 | Yes | 0.46193 | 0 | 0 | Group 2:Requires conductor upgrades | 228000 | 0 | 152000 | 131406.003 | 0 | 0 |  |  | 511406.003
Clarkwild West | 13459 | RelayMicroProcessor | 13459-90020684 | 1180 | 363 | 817 | 3.9049 | 3 | 3 | Clarkwild West | 13461 | RelayMicroProcessor | 10485070 | 95 | ESA | 1 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 3.2987 | 0 | 0 | 97.85% | 336 ACSR | 528.3955 | 97.85% | 336 ACSR | 12.0807 | 528.3953 | 540 | 97.85% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 228000 | 0 | 0 | 445660.9856 |  |  | 901660.9856
Peach W | 13909 | RelayMicroProcessor | 13909-73506050 | 774 | 311 | 463 | 3.3791 | 3 | 2 | Clarkwild West | 13461 | RelayMicroProcessor | 93113056 | 296 | ESA | 2 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 3.2987 | 0 | 0 | 113.5% | 4/0 AAAC | 465.21 | 104.7% | 336 ACSR | 12.9231 | 565.2371 | 540 | 104.7% | 0.40019 | No | 0.066856 | 0 | 0.33333 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 152000 | 126606.581 | 0 | 445660.9856 |  |  | 952267.5666
30th St W | 13158 | RelayElectromechanical | 13158-73208434 | 1845 | 305 | 1540 | 4.4064 | 3 | 5 | 56th St N | 13468 | RelayMicroProcessor | 60011830 | 86 | CSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 6.0766 | 0 | 0 | 81.71% | 4/0 AAAC | 334.9952 | 81.71% | 4/0 AAAC | 7.659 | 334.9952 | 410 | 0.81706 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 380000 | 0 | 0 | 0 |  |  | 728000
Temple Terrace S | 13205 | RelayElectromechanical | 13205-10054573 | 842 | 301 | 541 | 1.5727 | 3 | 2 | 56th St N | 13468 | RelayMicroProcessor | 93522354 | 250 | CSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 6.0766 | 0 | 0 | 50.1% | 4/0 AAAC | 205.4245 | 50.1% | 4/0 AAAC | 4.6966 | 205.4245 | 410 | 0.50104 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 152000 | 0 | 0 | 0 |  |  | 500000
Gordonville | 13031 | RelayElectromechanical | 13031-74014951 | 856 | 386 | 470 | 1.7724 | 3 | 2 | South Eloise | 13473 | RelayElectromechanical | 60176338 | 135 | WHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 6.1151 | 0 | 0 | 59.67% | 336 ACSR | 322.2437 | 59.67% | 336 ACSR | 7.3675 | 322.2437 | 540 | 0.59675 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 240000 | 152000 | 0 | 0 | 0 |  |  | 620000
DBL_BRCH S | 13193 | RelayMicroProcessor | 13193-74204470 | 905 | 342 | 563 | 2.9532 | 3 | 2 | WOODLAND E | 13484 | RelayElectromechanical | 60113802 | 142 | WSA | 5 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 8.7607 | 0 | 0 | 68.63% | 336 ACSR | 370.6232 | 68.63% | 336 ACSR | 8.4733 | 370.6118 | 540 | 0.68632 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 152000 | 0 | 0 | 0 |  |  | 500000
Del Webb S | 13488 | RelayElectromechanical | 13488-10730843 | 2812 | 406 | 2406 | 6.0141 | 3 | 7 | Del Webb S | 13489 | RelayMicroProcessor | 60203854 | 7 | SHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 22.4 | 6.449 | 0 | 0 | 80.97% | SGBUS | 455.8494 | 80.97% | SGBUS | 10.4221 | 455.8494 | 563 | 0.80968 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 532000 | 0 | 0 | 0 |  |  | 880000
MEADOWPK E | 13670 | RelayMicroProcessor | 13670-74201966 | 625 | 236 | 389 | 1.3215 | 3 | 2 | JACKSON W | 13490 | RelayElectromechanical | 60323409 | 247 | WSA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 6.5247 | 0 | 0 | 52.03% | 336 ACSR | 280.9884 | 52.03% | 336 ACSR | 6.4243 | 280.9884 | 540 | 0.52035 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 152000 | 0 | 0 | 0 |  |  | 500000
ROCKY_CR S | 13426 | RelayMicroProcessor | 13426-73302884 | 1807 | 292 | 1515 | 6.3889 | 3 | 5 | JACKSON W | 13491 | RelayElectromechanical | 60141069 | 108 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 6.5247 | 0 | 0 | 110.2% | 336 ACSR | 595.2111 | 110.2% | 336 ACSR | 13.6084 | 595.2113 | 540 | 110.2% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 380000 | 0 | 0 | 445660.9856 |  |  | 1173660.9856
GEORG_RD S | 13517 | RelayMicroProcessor | 13517-73203565 | 1467 | 309 | 1158 | 5.3423 | 3 | 4 | JACKSON W | 13493 | RelayElectromechanical | 60163127 | 114 | WSA | 4 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 6.5247 | 0 | 0 | 67.64% | 336 ACSR | 365.2423 | 67.64% | 336 ACSR | 8.3505 | 365.2417 | 540 | 0.67637 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 304000 | 0 | 0 | 0 |  |  | 652000
Madison N | 13172 | RelayMicroProcessor | 13172-75156131 | 615 | 314 | 301 | 2.1657 | 3 | 1 | Madison N | 13495 | RelayMicroProcessor | 92855067 | 268 | ESA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 24.1613 | 0 | 0 | 46.52% | 336 ACSR | 251.1996 | 46.52% | 336 ACSR | 5.7432 | 251.1996 | 540 | 0.46518 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 76000 | 0 | 0 | 0 |  |  | 304000
GEORG_RD N | 13514 | RelayElectromechanical | 13514-91870479 | 630 | 378 | 252 | 1.63 | 3 | 1 | GEORG_RD S | 13512 | RelayMicroProcessor | 91221103 | 297 | WSA | 3 | Adjacent XFM loaded over 100% | GEORG_RD S transformer upgrade | 28 | 1.5631 | 0 | 0 | 66.91% | 336 ACSR | 361.3059 | 66.91% | 336 ACSR | 8.2606 | 361.3059 | 540 | 0.66909 | 0 | No | 0 | 0 | 0 | Group 3: Requires transformer upgrade | 228000 | 120000 | 76000 | 0 | 1750000 | 0 |  |  | 2174000
JACKSON E | 13156 | RelayElectromechanical | 13156-73203779 | 1256 | 310 | 946 | 4.0475 | 3 | 3 | GEORG_RD S | 13512 | RelayMicroProcessor | 10004032 | 53 | WSA | 2 | Adjacent XFM loaded over 100% | GEORG_RD S transformer upgrade | 28 | 1.5631 | 0 | 0 | 85.73% | 336 ACSR | 462.9472 | 85.73% | 336 ACSR | 10.5844 | 462.9472 | 540 | 0.85731 | 0 | No | 0 | 0 | 0 | Group 3: Requires transformer upgrade | 228000 | 120000 | 228000 | 0 | 1750000 | 0 |  |  | 2326000
JACKSON E | 13154 | RelayElectromechanical | 13154-73001661 | 1857 | 299 | 1558 | 4.6432 | 3 | 5 | GEORG_RD S | 13512 | RelayMicroProcessor | 60450538 | 83 | WSA | 5 | Adjacent XFM loaded over 100% | GEORG_RD S transformer upgrade | 28 | 1.5631 | 0 | 0 | 91.52% | 336 ACSR | 494.2106 | 91.5% | 336 ACSR | 11.2964 | 494.0896 | 540 | 91.5% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 380000 | 0 | 1750000 | 445660.9856 |  |  | 2923660.9856
GEORG_RD S | 13510 | RelayMicroProcessor | 13510-72700706 | 1510 | 330 | 1180 | 5.1026 | 3 | 4 | GEORG_RD S | 13517 | RelayMicroProcessor | 10219171 | 52 | WSA | 2 | Adjacent XFM loaded over 100% | GEORG_RD S transformer upgrade | 28 | 1.5631 | 0 | 0 | 96.82% | 336 ACSR | 522.8073 | 96.81% | 336 ACSR | 11.9521 | 522.7692 | 540 | 96.81% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 304000 | 0 | 1750000 | 445660.9856 |  |  | 2727660.9856
JACKSON W | 13493 | RelayElectromechanical | 13493-73003543 | 670 | 323 | 347 | 1.5355 | 3 | 1 | GEORG_RD S | 13517 | RelayMicroProcessor | 60163127 | 225 | WSA | 5 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 1.5631 | 0 | 0 | 109.9% | 2 AAAC | 219.7969 | 81.3% | 336 ACSR | 10.0375 | 439.0246 | 540 | 0.81301 | 0.1339 | Yes | 0.1339 | 1 | 0 | Group 2:Requires conductor upgrades | 228000 | 120000 | 76000 | 50494.039 | 0 | 0 |  |  | 474494.039
IVY_ST | 13066 | #N/A | 13066-73302496 | 565 | 226 | 339 | 1.359 | 3 | 1 | STADIUM | 13519 | RelayElectromechanical | 60102295 | 287 | WSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 11.9869 | 0 | 0 | 68.7% | 2 AAAC | 137.3915 | 68.7% | 2 AAAC | 3.1412 | 137.3912 | 200 | 0.68696 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 240000 | 76000 | 0 | 0 | 0 |  |  | 544000
HYDE_PRK N | 13140 | RelayMicroProcessor | 13140-74303076 | 1268 | 373 | 895 | 2.5804 | 3 | 3 | ROME (2021) | 13523 | RelayMicroProcessor | 93694202 | 145 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 7.0323 | 0 | 0 | 83.59% | 2 AAAC | 167.1825 | 83.59% | 2 AAAC | 3.8223 | 167.1825 | 200 | 0.83591 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 228000 | 0 | 0 | 0 |  |  | 456000
COOLIDGE E | 13077 | RelayMicroProcessor | 13077-91148397 | 954 | 241 | 713 | 4.5696 | 3 | 3 | COOLIDGE W | 13531 | RelayMicroProcessor | 60160822 | 299 | WSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 19.2857 | 0.3 | 13.1216 | 117.6% | 2 AAAC | 235.1891 | 43.55% | 336 ACSR | 5.3772 | 235.1928 | 540 | 0.45984 | 0.00018939 | Yes | 0.00018939 | 0 | 0 | Group 2:Requires conductor upgrades | 228000 | 0 | 228000 | 53.877 | 0 | 0 |  |  | 456053.877
COOLIDGE E | 13079 | RelayElectromechanical | 13079-72802033 | 1440 | 323 | 1117 | 5.4525 | 3 | 4 | COOLIDGE W | 13533 | RelayElectromechanical | 60531757 | 111 | WSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 19.2857 | 0 | 0 | 90.92% | 336 ACSR | 490.9772 | 90.92% | 336 ACSR | 11.2252 | 490.9772 | 540 | 90.92% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 240000 | 304000 | 0 | 0 | 445660.9856 |  |  | 1217660.9856
HABANA S | 13218 | RelayMicroProcessor | 13218-60124034 | 1444 | 343 | 1101 | 3.3196 | 3 | 4 | COOLIDGE W | 13533 | RelayElectromechanical | 13218-93714821 | 37 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 19.2857 | 0 | 0 | 73.46% | 336 ACSR | 396.6869 | 73.46% | 336 ACSR | 9.0695 | 396.6869 | 540 | 0.73461 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 304000 | 0 | 0 | 0 |  |  | 652000
WATERS W | 13334 | RelayMicroProcessor | 13334-74004887 | 920 | 318 | 602 | 3.7628 | 3 | 2 | COOLIDGE W | 13533 | RelayElectromechanical | 91799510 | 300 | WSA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 19.2857 | 0 | 0 | 135% | 1/0 ALCN | 222.7101 | 81.19% | 336 ACSR | 10.0238 | 438.4287 | 540 | 0.8119 | 0.35871 | Yes | 0.082197 | 0 | 0.27652 | Group 2:Requires conductor upgrades | 228000 | 120000 | 152000 | 112631.7544 | 0 | 0 |  |  | 612631.7544
South Seffner W | 13577 | RelayMicroProcessor | 13577-74106756 | 1048 | 476 | 572 | 2.5095 | 3 | 2 | South Seffner W | 13576 | RelayElectromechanical | 90838010 | 115 | ESA | 2 | Adjacent XFM loaded over 100% | South Seffner W transformer upgrade | 22.4 | 1.2265 | 0 | 0 | 90.87% | 336 ACSR | 490.6741 | 90.87% | 336 ACSR | 11.2183 | 490.6741 | 540 | 90.87% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 152000 | 0 | 1750000 | 445660.9856 |  |  | 2695660.9856
Brandon W | 13229 | RelayMicroProcessor | 13229-91807284 | 1407 | 340 | 1067 | 3.6559 | 3 | 4 | South Seffner W | 13577 | RelayMicroProcessor | 10457914 | 124 | ESA | 3 | Adjacent XFM loaded over 100% | South Seffner W transformer upgrade | 22.4 | 1.2265 | 0 | 0 | 70.4% | 336 ACSR | 380.1799 | 70.4% | 336 ACSR | 8.6921 | 380.1797 | 540 | 0.70404 | 0 | No | 0 | 0 | 0 | Group 3: Requires transformer upgrade | 228000 | 0 | 304000 | 0 | 1750000 | 0 |  |  | 2282000
Saint Cloud S | 13795 | RelayMicroProcessor | 13795-75656723 | 1530 | 258 | 1272 | 6.9182 | 3 | 4 | South Seffner W | 13579 | RelayElectromechanical | 93032926 | 235 | ESA | 4 | Adjacent XFM loaded over 100% | South Seffner W transformer upgrade | 22.4 | 1.2265 | 0 | 0 | 219.1% | 2 AAAC | 438.207 | 123% | 336 ACSR | 15.1881 | 664.3054 | 540 | 123% | 0.0066288 | No | 0.0066288 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 304000 | 1885.695 | 1750000 | 445660.9856 |  |  | 2849546.6806
South Seffner E | 13128 | RelayMicroProcessor | 13128-74105975 | 1332 | 314 | 1018 | 4.4926 | 3 | 3 | South Seffner W | 13579 | RelayElectromechanical | 10507404 | 79 | ESA | 1 | Adjacent XFM loaded over 100% | South Seffner W transformer upgrade | 22.4 | 1.2265 | 0 | 0 | 109% | 336 ACSR | 588.4087 | 109% | 336 ACSR | 13.4527 | 588.404 | 540 | 109% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 228000 | 0 | 1750000 | 445660.9856 |  |  | 2771660.9856
D_MABRY E | 13587 | RelayMicroProcessor | 13587-74550745 | 2319 | 356 | 1963 | 6.7604 | 3 | 6 | D_MABRY W | 13582 | RelayMicroProcessor | 94030114 | 67 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 7.734 | 0 | 0 | 191.4% | 2 AAAC | 382.8023 | 141.1% | 336 ACSR | 17.4183 | 761.8533 | 540 | 141.1% | 0.0030303 | No | 0.0030303 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 456000 | 862.032 | 0 | 445660.9856 |  |  | 1130523.0176
EHRLICH E | 13891 | RelayMicroProcessor | 92977818 | 1382 | 347 | 1035 | 4.9474 | 3 | 3 | D_MABRY W | 13585 | RelayMicroProcessor | 92696158 | 202 | WSA | 4 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 7.734 | 0 | 0 | 83.55% | 336 ACSR | 451.1929 | 83.55% | 336 ACSR | 10.3156 | 451.1902 | 540 | 0.83554 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 228000 | 0 | 0 | 0 |  |  | 456000
EHRLICH E | 13892 | RelayMicroProcessor | 13892-74201818 | 1019 | 271 | 748 | 5.8412 | 3 | 3 | D_MABRY E | 13587 | RelayMicroProcessor | 60245404 | 294 | WSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 9.6294 | 0 | 0 | 108.3% | 336 ACSR | 584.9094 | 108.3% | 336 ACSR | 13.3728 | 584.9094 | 540 | 108.3% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 228000 | 0 | 0 | 445660.9856 |  |  | 901660.9856
Seneca N | 13591 | RelayMicroProcessor | 13591-75553035 | 1878 | 306 | 1572 | 7.5104 | 3 | 5 | Seneca N | 13590 | RelayMicroProcessor | 91439165 | 137 | CSA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 12.5485 | 0 | 0 | 120.4% | 336 ACSR | 650.1148 | 120.4% | 336 ACSR | 14.8636 | 650.1148 | 540 | 120.4% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 380000 | 0 | 0 | 445660.9856 |  |  | 1053660.9856
Yukon S | 13102 | RelayMicroProcessor | 13102-75353082 | 1190 | 367 | 823 | 2.8775 | 3 | 3 | Seneca N | 13591 | RelayMicroProcessor | 91420049 | 78 | CSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 12.5485 | 0.1 | 4.3739 | 87.92% | 336 ACSR | 474.7533 | 87.92% | 336 ACSR | 10.8543 | 474.7534 | 540 | 0.88727 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 228000 | 0 | 0 | 0 |  |  | 456000
Juneau E | 13417 | RelayMicroProcessor | 13417-73502987 | 903 | 306 | 597 | 2.8415 | 3 | 2 | Seneca N | 13592 | RelayMicroProcessor | 92761925 | 193 | CSA | 4 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 12.5485 | 0 | 0 | 67.83% | 1/0 ALCN | 111.9176 | 66.56% | 4/0 ALJCN | 3.4698 | 151.7631 | 228 | 0.66563 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 152000 | 0 | 0 | 0 |  |  | 380000
Seneca N | 13593 | RelayMicroProcessor | 13593-75804370 | 878 | 304 | 574 | 2.9682 | 3 | 2 | Seneca N | 13592 | RelayMicroProcessor | 90876958 | 156 | CSA | 6 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 12.5485 | 0 | 0 | 91.56% | 4/0 ALJCN | 208.7654 | 63.91% | 336 ACSR | 7.89 | 345.0982 | 540 | 0.63907 | 0.059659 | Yes | 0 | 0 | 0.059659 | Group 2:Requires conductor upgrades | 228000 | 0 | 152000 | 19255.8068 | 0 | 0 |  |  | 399255.8068
Juneau E | 13418 | RelayMicroProcessor | 13418-75801229 | 1656 | 292 | 1364 | 5.0508 | 3 | 4 | Seneca N | 13593 | RelayMicroProcessor | 92299713 | 35 | CSA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 12.5485 | 0 | 0 | 73.66% | 336 ACSR | 397.7415 | 73.66% | 336 ACSR | 9.0936 | 397.7415 | 540 | 0.73656 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 304000 | 0 | 0 | 0 |  |  | 532000
McFarland | 13105 | RelayMicroProcessor | 13105-10581158 | 1173 | 411 | 762 | 5.3782 | 3 | 3 | Seneca N | 13593 | RelayMicroProcessor | 13105-93058315 | 243 | CSA | 4 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 12.5485 | 0 | 0 | 76.92% | 336 ACSR | 415.3508 | 76.92% | 336 ACSR | 9.4962 | 415.3508 | 540 | 0.76917 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 228000 | 0 | 0 | 0 |  |  | 456000
Pine Lake N | 13186 | RelayMicroProcessor | 13186-75050350 | 702 | 317 | 385 | 2.0235 | 3 | 2 | Seneca N | 13593 | RelayMicroProcessor | 92357564 | 216 | CSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 12.5485 | 0 | 0 | 46.89% | 336 ACSR | 253.1818 | 46.89% | 336 ACSR | 5.7885 | 253.1818 | 540 | 0.46886 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 152000 | 0 | 0 | 0 |  |  | 380000
Pine Lake S | 13632 | RelayElectromechanical | 13632-74751502 | 728 | 490 | 238 | 1.4184 | 3 | 1 | Seneca N | 13593 | RelayMicroProcessor | 13593-93054964 | 207 | CSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 12.5485 | 0 | 0 | 47.77% | 336 ACSR | 257.9585 | 47.77% | 336 ACSR | 5.8977 | 257.9584 | 540 | 0.4777 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 76000 | 0 | 0 | 0 |  |  | 424000
Fern St | 13045 | RelayMicroProcessor | 13045-74010001 | 1235 | 304 | 931 | 3.3979 | 3 | 3 | 30th St W | 13600 | RelayMicroProcessor | 10094496 | 92 | CSA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 8.2315 | 0 | 0 | 139.6% | 2/0 AAAC | 432.7797 | 88.65% | 2/0 AAAC | 6.2833 | 274.8227 | 310 | 0.88652 | 0.24148 | Yes | 0.24148 | 0 | 0 | Group 2:Requires conductor upgrades | 228000 | 0 | 228000 | 68693.175 | 0 | 0 |  |  | 524693.175
HIMES E | 13062 | RelayMicroProcessor | 13062-74307156 | 773 | 347 | 426 | 1.4049 | 3 | 2 | MACDILL E | 13605 | RelayMicroProcessor | 60029463 | 200 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 34.4444 | 0 | 0 | 58.48% | 2/0 AAAC | 181.2901 | 58.48% | 2/0 AAAC | 4.1448 | 181.2901 | 310 | 0.58481 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 152000 | 0 | 0 | 0 |  |  | 380000
MANHATTAN E | 13111 | RelayMicroProcessor | 13111-74305719 | 898 | 296 | 602 | 1.7155 | 3 | 2 | EL_PRADO | 13611 | RelayElectromechanical | 60072681 | 151 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 10.6812 | 0 | 0 | 47.72% | 4/0 AAAC | 195.6384 | 47.72% | 4/0 AAAC | 4.4729 | 195.6384 | 410 | 0.47717 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 152000 | 0 | 0 | 0 |  |  | 500000
KEYSTONE E | 13070 | RelayMicroProcessor | 13070-75050757 | 651 | 296 | 355 | 2.332 | 3 | 2 | WAYNE_RD | 13621 | RelayMicroProcessor | 10026544 | 298 | WSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 10.3406 | 0 | 0 | 49.84% | 1000 ALJCN | 275.6013 | 49.84% | 1000 ALJCN | 6.3011 | 275.6013 | 553 | 0.49837 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 152000 | 0 | 0 | 0 |  |  | 380000
TRKYFORD | 13677 | RelayElectromechanical | 13677-60416617 | 1129 | 307 | 822 | 5.3449 | 3 | 3 | WAYNE_RD | 13621 | RelayMicroProcessor | 13621-93126871 | 255 | WSA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 10.3406 | 0 | 0 | 70.94% | 336 ACSR | 383.0542 | 70.94% | 336 ACSR | 8.7578 | 383.0542 | 540 | 0.70936 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 228000 | 0 | 0 | 0 |  |  | 576000
Florida Ave N | 13837 | RelayMicroProcessor | 13837-72602032 | 1084 | 276 | 808 | 4.2201 | 3 | 3 | Pine Lake S | 13630 | RelayMicroProcessor | 60130389 | 175 | CSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 4.8969 | 0 | 0 | 87.39% | 336 ACSR | 471.911 | 87.39% | 336 ACSR | 10.7893 | 471.911 | 540 | 0.87391 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 228000 | 0 | 0 | 0 |  |  | 456000
Florida Ave S | 13835 | RelayMicroProcessor | 13835-74853192 | 1388 | 232 | 1156 | 2.6224 | 3 | 4 | Pine Lake S | 13630 | RelayMicroProcessor | 60344887 | 65 | CSA | 4 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 4.8969 | 0 | 0 | 78.84% | 336 ACSR | 425.7347 | 78.84% | 336 ACSR | 9.7336 | 425.7347 | 540 | 0.7884 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 304000 | 0 | 0 | 0 |  |  | 532000
Pine Lake N | 13185 | RelayMicroProcessor | 13185-74005784 | 1373 | 310 | 1063 | 2.7115 | 3 | 4 | Pine Lake N | 13633 | RelayElectromechanical | 10378362 | 32 | CSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 6.9134 | 0 | 0 | 81.95% | 2 AAAC | 163.9023 | 81.95% | 2 AAAC | 3.7473 | 163.8997 | 200 | 0.8195 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 304000 | 0 | 0 | 0 |  |  | 652000
Riverview S | 14023 | RelayMicroProcessor | 14023-75707442 | 1175 | 302 | 873 | 3.9332 | 3 | 3 | Rhodine North | 13648 | RelayMicroProcessor | 60316214 | 150 | SHA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 6.4778 | 0 | 0 | 93.28% | 2 AAAC | 186.562 | 88.4% | 336 ACSR | 10.9141 | 477.3679 | 540 | 0.88401 | 0.00018939 | Yes | 0.00018939 | 0 | 0 | Group 2:Requires conductor upgrades | 228000 | 0 | 228000 | 53.877 | 0 | 0 |  |  | 456053.877
Lake Ruby North | 13922 | RelayMicroProcessor | 13922-75153599 | 2381 | 279 | 2102 | 6.4666 | 3 | 7 | Lake Winterset E | 13661 | RelayElectromechanical | 92771258 | 39 | WHA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 8.4823 | 0 | 0 | 135.8% | 2/0 AAAC | 420.8545 | 131.1% | 336 ACSR | 16.1832 | 707.8314 | 540 | 131.1% | 0.033523 | No | 0.033523 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 532000 | 9536.229 | 0 | 445660.9856 |  |  | 1335197.2146
Lake Ruby South | 13918 | RelayMicroProcessor | 13918-90021019 | 854 | 313 | 541 | 2.3506 | 3 | 2 | Lake Winterset E | 13661 | RelayElectromechanical | 90992308 | 203 | WHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 8.4823 | 0 | 0 | 98.21% | 336 ACSR | 530.3365 | 98.21% | 336 ACSR | 12.125 | 530.332 | 540 | 98.21% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 152000 | 0 | 0 | 445660.9856 |  |  | 945660.9856
JACKSON W | 13490 | RelayElectromechanical | 13490-73002153 | 961 | 334 | 627 | 2.6743 | 3 | 2 | MEADOWPK E | 13670 | RelayMicroProcessor | 60323409 | 214 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 4.7505 | 0 | 0 | 46.88% | 2 AAAC | 93.7666 | 46.88% | 2 AAAC | 2.1438 | 93.7666 | 200 | 0.46883 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 152000 | 0 | 0 | 0 |  |  | 500000
JACKSON E | 13155 | RelayElectromechanical | 13155-90619398 | 1778 | 303 | 1475 | 5.7468 | 3 | 5 | MEADOWPK E | 13671 | RelayMicroProcessor | 60156529 | 113 | WSA | 3 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 4.7505 | 0 | 0 | 129.9% | 4/0 ALJCN | 296.1173 | 106.6% | 336 ACSR | 13.1641 | 575.7821 | 540 | 106.6% | 1.1021 | No | 0 | 0 | 1.1021 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 380000 | 355712.825 | 0 | 445660.9856 |  |  | 1529373.8106
MEADOWPK E | 13669 | RelayMicroProcessor | 13669-73500848 | 1379 | 286 | 1093 | 4.2334 | 3 | 4 | MEADOWPK E | 13672 | RelayMicroProcessor | 60471837 | 47 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 4.7505 | 0 | 0 | 116.6% | 2/0 AAAC | 361.5551 | 101.8% | 336 ACSR | 12.5665 | 549.6398 | 540 | 101.8% | 0.0011364 | No | 0.0011364 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 304000 | 323.262 | 0 | 445660.9856 |  |  | 977984.2476
WSTCHASE E (69kV) | 14080 | RelayMicroProcessor | 60161906 | 1375 | 483 | 892 | 5.3428 | 3 | 3 | MEADOWPK W | 13673 | RelayMicroProcessor | 93628468 | 186 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 17.6595 | 0.754 | 32.9789 | 82.42% | 1/0 ALCN | 135.9962 | 82.42% | 1/0 ALCN | 3.1093 | 135.9962 | 165 | 1.0241 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 228000 | 0 | 0 | 0 |  |  | 456000
MEADOWPK W | 13673 | RelayMicroProcessor | 13673-73500879 | 991 | 498 | 493 | 1.2898 | 3 | 2 | MEADOWPK W | 13674 | RelayMicroProcessor | 60364708 | 51 | WSA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 17.6595 | 0 | 0 | 57.92% | 336 ACSR | 312.7613 | 57.92% | 336 ACSR | 7.1507 | 312.7613 | 540 | 0.57919 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 152000 | 0 | 0 | 0 |  |  | 380000
ROCKY_CR N | 13575 | RelayMicroProcessor | 13575-74403022 | 635 | 258 | 377 | 1.3157 | 3 | 2 | MEADOWPK W | 13674 | RelayMicroProcessor | 60122125 | 257 | WSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 17.6595 | 0 | 0 | 66.55% | 336 ACSR | 359.361 | 66.55% | 336 ACSR | 8.2161 | 359.361 | 540 | 0.66548 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 152000 | 0 | 0 | 0 |  |  | 380000
SUNLAKE | 14069 | RelayMicroProcessor | 14069-94025195 | 1451 | 484 | 967 | 6.024 | 3 | 3 | TRKYFORD | 13677 | RelayElectromechanical | 60354217 | 267 | WSA | 2 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 10.6863 | 0 | 0 | 103.9% | 336 ACSR | 560.9168 | 103.9% | 336 ACSR | 12.8243 | 560.9168 | 540 | 103.9% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 228000 | 0 | 0 | 445660.9856 |  |  | 1021660.9856
TRKYFORD | 13679 | RelayMicroProcessor | 13679-73503141 | 1339 | 225 | 1114 | 7.5093 | 3 | 4 | TRKYFORD | 13678 | RelayMicroProcessor | 60026827 | 286 | WSA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 10.6863 | 0.754 | 32.9789 | 290.2% | 1/0 ALCN | 478.7798 | 125.1% | 1000 ALJCN | 15.8192 | 691.912 | 553 | 131.1% | 2.0307 | No | 0.54848 | 1 | 1.4822 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 304000 | 646830.6147 | 0 | 445660.9856 |  |  | 1624491.6003
D_MABRY E | 13586 | RelayMicroProcessor | 13586-74851131 | 1347 | 381 | 966 | 5.0552 | 3 | 3 | TRKYFORD | 13679 | RelayMicroProcessor | 60303647 | 229 | WSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 10.6863 | 0 | 0 | 109.5% | 336 ACSR | 591.0563 | 109.5% | 336 ACSR | 13.5128 | 591.0329 | 540 | 109.5% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 228000 | 0 | 0 | 445660.9856 |  |  | 901660.9856
EHRLICH W | 13888 | RelayElectromechanical | 13888-73502608 | 1164 | 280 | 884 | 4.0934 | 3 | 3 | TRKYFORD | 13679 | RelayMicroProcessor | 10266560 | 102 | WSA | 4 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 10.6863 | 0 | 0 | 101.1% | 336 ACSR | 545.7984 | 101.1% | 336 ACSR | 12.4781 | 545.7745 | 540 | 101.1% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 228000 | 0 | 0 | 445660.9856 |  |  | 1021660.9856
Bloomingdale S | 13040 | RelayMicroProcessor | 13040-91392266 | 1087 | 270 | 817 | 3.6652 | 3 | 3 | Pearson S | 13685 | RelayElectromechanical | 93288488 | 258 | ESA | 1 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 2.0847 | 0 | 0 | 99.97% | 336 ACSR | 539.8347 | 99.97% | 336 ACSR | 12.3423 | 539.8347 | 540 | 99.97% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 228000 | 0 | 0 | 445660.9856 |  |  | 1021660.9856
Saint Cloud N | 13797 | RelayMicroProcessor | 13797-10921565 | 1506 | 326 | 1180 | 7.0516 | 3 | 4 | Pearson S | 13686 | RelayElectromechanical | 10840529 | 277 | ESA | 2 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 2.0847 | 0 | 0 | 124.1% | 336 ACSR | 669.9766 | 124.1% | 336 ACSR | 15.3177 | 669.9766 | 540 | 124.1% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 304000 | 0 | 0 | 445660.9856 |  |  | 1097660.9856
Bloomingdale N | 14109 | RelayMicroProcessor | 14109-74017930 | 690 | 401 | 289 | 2.0865 | 3 | 1 | Pearson N | 13690 | RelayMicroProcessor | 10549348 | 212 | ESA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 4.9083 | 0 | 0 | 72.71% | 336 ACSR | 392.6359 | 72.71% | 336 ACSR | 8.9769 | 392.6359 | 540 | 0.7271 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 76000 | 0 | 0 | 0 |  |  | 304000
Pearson N | 13693 | RelayMicroProcessor | 13693-75855011 | 895 | 311 | 584 | 3.541 | 3 | 2 | Pearson N | 13690 | RelayMicroProcessor | 10549343 | 233 | ESA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 4.9083 | 0 | 0 | 84.19% | 336 ACSR | 454.6446 | 84.19% | 336 ACSR | 10.3945 | 454.6435 | 540 | 0.84193 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 152000 | 0 | 0 | 0 |  |  | 380000
Bell Shoals | 13732 | RelayMicroProcessor | 60230211 | 1275 | 343 | 932 | 5.5398 | 3 | 3 | Pearson N | 13693 | RelayMicroProcessor | 60239010 | 290 | ESA | 5 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 4.9083 | 0 | 0 | 219.6% | 2 AAAC | 439.2717 | 104.4% | 336 ACSR | 12.8857 | 563.6022 | 540 | 104.4% | 0.013258 | No | 0.013258 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 228000 | 3771.39 | 0 | 445660.9856 |  |  | 905432.3756
Pearson N | 13690 | RelayMicroProcessor | 13690-74018163 | 904 | 471 | 433 | 4.2132 | 3 | 2 | Pearson N | 13693 | RelayMicroProcessor | 10549343 | 289 | ESA | 4 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 4.9083 | 0 | 0 | 176.3% | 2 AAAC | 352.6683 | 87.58% | 336 ACSR | 10.8123 | 472.9176 | 540 | 0.87577 | 0.013258 | Yes | 0.013258 | 0 | 0 | Group 2:Requires conductor upgrades | 228000 | 0 | 152000 | 3771.39 | 0 | 0 |  |  | 383771.39
Providence W | 13885 | RelayMicroProcessor | 13885-60311229 | 1198 | 312 | 886 | 3.9636 | 3 | 3 | Buckhorn N | 13707 | RelayMicroProcessor | 10108300 | 88 | ESA | 2 | Adjacent XFM loaded over 100% | Buckhorn N transformer upgrade | 28 | -1.4362 | 0 | 0 | 121.5% | 2/0 AAAC | 376.67 | 80.29% | 336 ACSR | 9.912 | 433.5395 | 540 | 0.80285 | 0.039205 | Yes | 0.039205 | 0 | 0 | Group 3: Requires transformer upgrade | 228000 | 0 | 228000 | 11152.539 | 1750000 | 0 |  |  | 2217152.539
Buckhorn S | 13706 | RelayMicroProcessor | 13706-76053012 | 1810 | 373 | 1437 | 4.164 | 3 | 5 | Buckhorn N | 13708 | RelayMicroProcessor | 92981833 | 158 | ESA | 2 | Adjacent XFM loaded over 100% | Buckhorn N transformer upgrade | 28 | -1.4362 | 0 | 0 | 147.8% | 4/0 ALJCN | 336.9303 | 120.7% | 336 ACSR | 14.8975 | 651.5971 | 540 | 120.7% | 2.3604 | No | 0.0035985 | 0 | 2.3568 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 380000 | 761719.7266 | 1750000 | 445660.9856 |  |  | 3565380.7122
Madison S | 13174 | RelayMicroProcessor | 13174-92097293 | 3091 | 376 | 2715 | 6.4656 | 3 | 8 | Buckhorn N | 13708 | RelayMicroProcessor | 13174-93310282 | 6 | ESA | 1 | Adjacent XFM loaded over 100% | Buckhorn N transformer upgrade | 28 | -1.4362 | 0 | 0 | 171.9% | 2/0 AAAC | 533.0061 | 130.9% | 336 ACSR | 16.167 | 707.1211 | 540 | 130.9% | 0.027273 | No | 0.027273 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 608000 | 7758.288 | 1750000 | 445660.9856 |  |  | 3039419.2736
Providence E | 13878 | RelayMicroProcessor | 13878-76104774 | 1585 | 475 | 1110 | 4.7804 | 3 | 4 | Buckhorn S | 13710 | RelayMicroProcessor | 13710-92883510 | 55 | ESA | 5 | Adjacent XFM loaded over 100% | Buckhorn S transformer upgrade | 37 | 0.32078 | 0 | 0 | 136.7% | 336 ACSR | 738.1886 | 136.7% | 336 ACSR | 16.8773 | 738.1905 | 540 | 136.7% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 304000 | 0 | 1750000 | 445660.9856 |  |  | 2727660.9856
Providence E | 13879 | RelayElectromechanical | 13879-76104656 | 2299 | 324 | 1975 | 5.4946 | 3 | 6 | Buckhorn S | 13711 | RelayMicroProcessor | 60615439 | 34 | ESA | 2 | Adjacent XFM loaded over 100% | Buckhorn S transformer upgrade | 37 | 0.32078 | 0 | 0 | 130.3% | 336 ACSR | 703.7301 | 130.3% | 336 ACSR | 16.0894 | 703.7301 | 540 | 130.3% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 456000 | 0 | 1750000 | 445660.9856 |  |  | 2999660.9856
Buckhorn N | 13709 | RelayMicroProcessor | 13709-90839264 | 1287 | 346 | 941 | 3.4117 | 3 | 3 | Buckhorn S | 13712 | RelayMicroProcessor | 10892848 | 60 | ESA | 1 | Adjacent XFM loaded over 100% | Buckhorn S transformer upgrade | 37 | 0.32078 | 0 | 0 | 76.39% | 336 ACSR | 412.5062 | 76.39% | 336 ACSR | 9.4312 | 412.5062 | 540 | 76.39% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 228000 | 0 | 1750000 | 445660.9856 |  |  | 2651660.9856
Chapman | 14268 | RelayMicroProcessor | 60384236 | 871 | 287 | 584 | 2.6454 | 3 | 2 | Tampa Palms E | 13715 | RelayMicroProcessor | 60383762 | 166 | CSA | 1 | Adjacent XFM loaded over 100% | Tampa Palms E transformer upgrade | 28 | -0.58112 | 0 | 0 | 82.05% | 1/0 ALCN | 135.3777 | 82.05% | 1/0 ALCN | 3.0951 | 135.3776 | 165 | 0.82047 | 0 | No | 0 | 0 | 0 | Group 3: Requires transformer upgrade | 228000 | 0 | 152000 | 0 | 1750000 | 0 |  |  | 2130000
Chapman | 14266 | RelayMicroProcessor | 14266-93042295 | 2601 | 323 | 2278 | 6.2182 | 3 | 7 | Tampa Palms E | 13715 | RelayMicroProcessor | 90389584 | 23 | CSA | 2 | Adjacent XFM loaded over 100% | Tampa Palms E transformer upgrade | 28 | -0.58112 | 0 | 0 | 188.9% | 1/0 ALCN | 311.6107 | 108.1% | 336 ACSR | 13.351 | 583.9539 | 540 | 108.1% | 0.32746 | No | 0.0098485 | 0 | 0.31761 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 532000 | 105315.8517 | 1750000 | 445660.9856 |  |  | 3060976.8373
Chapman | 14267 | RelayMicroProcessor | 91259736 | 1599 | 221 | 1378 | 4.731 | 3 | 4 | Tampa Palms E | 13717 | RelayMicroProcessor | 60354987 | 131 | CSA | 1 | Adjacent XFM loaded over 100% | Tampa Palms E transformer upgrade | 28 | -0.58112 | 0 | 0 | 139.7% | 1/0 ALCN | 230.439 | 84.68% | 336 ACSR | 10.4542 | 457.2514 | 540 | 0.84676 | 0.52936 | Yes | 0 | 0 | 0.52936 | Group 3: Requires transformer upgrade | 228000 | 0 | 304000 | 170857.0795 | 1750000 | 0 |  |  | 2452857.0795
Kirkland | 13389 | RelayMicroProcessor | 13389-73104831 | 1195 | 324 | 871 | 3.7906 | 3 | 3 | Gallagher N | 13724 | RelayElectromechanical | 90348996 | 85 | PCA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 22.4 | 4.8206 | 0 | 0 | 91.27% | 336 ACSR | 492.8347 | 91.26% | 336 ACSR | 11.2675 | 492.8252 | 540 | 91.26% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 228000 | 0 | 0 | 445660.9856 |  |  | 1021660.9856
Bell Shoals | 13729 | RelayMicroProcessor | 13729-92964899 | 1002 | 311 | 691 | 4.5281 | 3 | 2 | Bell Shoals | 13733 | RelayMicroProcessor | 93276107 | 208 | ESA | 1 | Adjacent XFM loaded over 100% | Bell Shoals transformer upgrade | 27.8 | -1.9025 | 0 | 0 | 158% | 1/0 ALCN | 260.7691 | 115.6% | 336 ACSR | 14.2758 | 624.4025 | 540 | 115.6% | 0.3678 | No | 0.0037879 | 0 | 0.36402 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 152000 | 118568.5264 | 1750000 | 445660.9856 |  |  | 2694229.512
GRAY_ST N | 13199 | RelayElectromechanical | 13199-60575710 | 1095 | 333 | 762 | 3.0236 | 3 | 3 | CLEARVIEW S | 13737 | RelayMicroProcessor | 93188744 | 125 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 3.5087 | 1 | 43.7387 | 59.32% | 336 ACSR | 320.3378 | 59.32% | 336 ACSR | 7.3239 | 320.3378 | 540 | 0.67422 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 228000 | 0 | 0 | 0 |  |  | 576000
CARROLWD E | 13539 | RelayElectromechanical | 13539-75650010 | 1095 | 397 | 698 | 3.1133 | 3 | 2 | CASEY_RD N | 13745 | RelayMicroProcessor | 60023075 | 97 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 9.9473 | 0 | 0 | 83.82% | 336 ACSR | 452.6218 | 83.82% | 336 ACSR | 10.3483 | 452.6218 | 540 | 0.83819 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 152000 | 0 | 0 | 0 |  |  | 500000
CASEY_RD N | 13747 | RelayMicroProcessor | 13747-75250111 | 629 | 301 | 328 | 2.4888 | 3 | 1 | CASEY_RD N | 13748 | RelayMicroProcessor | 90424786 | 265 | WSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 9.9473 | 0 | 0 | 78.17% | 336 ACSR | 422.1222 | 78.17% | 336 ACSR | 9.651 | 422.1222 | 540 | 0.78171 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 76000 | 0 | 0 | 0 |  |  | 304000
WATERS E | 13332 | RelayMicroProcessor | 13332-10756374 | 1798 | 306 | 1492 | 4.7514 | 3 | 5 | CASEY_RD S | 13749 | RelayMicroProcessor | 10756225 | 18 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 21.4337 | 0 | 0 | 96.98% | 336 ACSR | 523.7058 | 96.98% | 336 ACSR | 11.9735 | 523.7058 | 540 | 96.98% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 380000 | 0 | 0 | 445660.9856 |  |  | 1053660.9856
EL_PRADO | 13610 | RelayElectromechanical | 13610-74306456 | 1370 | 344 | 1026 | 4.2051 | 3 | 3 | GRANADA | 13753 | RelayMicroProcessor | 10092441 | 74 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 10.0845 | 0 | 0 | 76.64% | 336 ACSR | 413.874 | 76.64% | 336 ACSR | 9.4624 | 413.874 | 540 | 0.76643 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 228000 | 0 | 0 | 0 |  |  | 576000
GRAY_ST N | 13201 | RelayElectromechanical | 13201-73000892 | 988 | 406 | 582 | 4.3604 | 3 | 2 | BOYSCOUT W | 13762 | RelayMicroProcessor | 93585705 | 204 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 13.7998 | 0 | 0 | 83.4% | 336 ACSR | 450.3525 | 83.4% | 336 ACSR | 10.2964 | 450.3525 | 540 | 0.83399 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 152000 | 0 | 0 | 0 |  |  | 500000
Berkley South | 13695 | RelayMicroProcessor | 13695-90706451 | 1728 | 469 | 1259 | 5.9191 | 3 | 4 | Lake Juliana | 13772 | RelayElectromechanical | 93531202 | 176 | WHA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 7.6039 | 0 | 0 | 82.28% | 336 ACSR | 444.3265 | 82.28% | 336 ACSR | 10.1587 | 444.3263 | 540 | 0.82283 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 304000 | 0 | 0 | 0 |  |  | 652000
Polk City | 13299 | RelayMicroProcessor | 13299-75452219 | 1810 | 390 | 1420 | 7.3177 | 3 | 5 | Lake Juliana | 13772 | RelayElectromechanical | 93760109 | 215 | WHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 7.6039 | 0 | 0 | 207.1% | 1/0 ALCN | 341.7498 | 93.52% | 336 ACSR | 11.5455 | 504.9868 | 540 | 93.52% | 0.48428 | No | 0 | 0 | 0.48428 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 380000 | 156308.2477 | 0 | 445660.9856 |  |  | 1329969.2333
Miller Mac | 13780 | RelayElectromechanical | 13780-76001460 | 1518 | 227 | 1291 | 6.3537 | 3 | 4 | Miller Mac | 13777 | RelayElectromechanical | 60201691 | 219 | SHA | 1 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 5.896 | 0 | 0 | 130.2% | 336 ACSR | 702.984 | 130.1% | 336 ACSR | 16.058 | 702.3535 | 540 | 130.1% | 0.70682 | No | 0.085606 | 0 | 0.62121 | Group 4: Requires multiple FLISR ties | 228000 | 240000 | 304000 | 224857.3131 | 0 | 445660.9856 |  |  | 1442518.2987
South Seffner W | 13579 | RelayElectromechanical | 13579-92390861 | 1687 | 235 | 1452 | 6.3698 | 3 | 5 | Saint Cloud S | 13795 | RelayMicroProcessor | 93032926 | 152 | ESA | 3 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 4.2864 | 0 | 0 | 121.9% | 336 ACSR | 658.1942 | 121.9% | 336 ACSR | 15.0482 | 658.1869 | 540 | 121.9% | 0.0066288 | No | 0.0066288 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 380000 | 1885.695 | 0 | 445660.9856 |  |  | 1175546.6806
Pearson S | 13687 | RelayElectromechanical | 13687-72706349 | 1739 | 389 | 1350 | 6.108 | 3 | 4 | Saint Cloud S | 13796 | RelayMicroProcessor | 10829764 | 189 | ESA | 5 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 4.2864 | 0 | 0 | 101.2% | 336 ACSR | 546.2211 | 104.2% | 336 ACSR | 12.8591 | 562.4406 | 540 | 104.2% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 304000 | 0 | 0 | 445660.9856 |  |  | 1097660.9856
Saint Cloud N | 13799 | RelayMicroProcessor | 13799-73212690 | 1911 | 307 | 1604 | 5.7706 | 3 | 5 | Saint Cloud S | 13796 | RelayMicroProcessor | 60159373 | 96 | ESA | 4 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 4.2864 | 0 | 0 | 104.2% | 336 ACSR | 562.4406 | 104.2% | 336 ACSR | 12.8591 | 562.4406 | 540 | 104.2% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 380000 | 0 | 0 | 445660.9856 |  |  | 1053660.9856
Bloomingdale S | 13041 | RelayMicroProcessor | 13041-92698749 | 1473 | 329 | 1144 | 6.4413 | 3 | 4 | Saint Cloud N | 13797 | RelayMicroProcessor | 93880887 | 264 | ESA | 1 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 3.1341 | 0 | 0 | 123.9% | 336 ACSR | 669.0242 | 123.9% | 336 ACSR | 15.2956 | 669.0072 | 540 | 123.9% | 0.026136 | No | 0.026136 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 304000 | 7435.026 | 0 | 445660.9856 |  |  | 985096.0116
Brandon E | 13231 | RelayMicroProcessor | 13231-76102792 | 1326 | 334 | 992 | 3.9964 | 3 | 3 | Saint Cloud N | 13798 | RelayMicroProcessor | 60256181 | 147 | ESA | 3 | Adjacent XFM loaded over 100% | Saint Cloud N transformer upgrade | 28 | 3.1341 | 0 | 0 | 88.03% | 336 ACSR | 475.3469 | 88.03% | 336 ACSR | 10.8679 | 475.3472 | 540 | 0.88027 | 0 | No | 0 | 0 | 0 | Group 3: Requires transformer upgrade | 228000 | 0 | 228000 | 0 | 1750000 | 0 |  |  | 2206000
Saint Cloud S | 13796 | RelayMicroProcessor | 13796-73212797 | 1601 | 384 | 1217 | 4.5008 | 3 | 4 | Saint Cloud N | 13799 | RelayMicroProcessor | 60159373 | 33 | ESA | 3 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 3.1341 | 0 | 0 | 109.3% | 336 ACSR | 590.2377 | 109.3% | 336 ACSR | 13.4946 | 590.2362 | 540 | 109.3% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 304000 | 0 | 0 | 445660.9856 |  |  | 977660.9856
Kirkland | 13391 | RelayMicroProcessor | 60312496 | 1754 | 318 | 1436 | 5.801 | 3 | 5 | Knights | 13805 | RelayMicroProcessor | 92481353 | 84 | PCA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 6.0354 | 0 | 0 | 97.97% | 336 ACSR | 529.0454 | 97.97% | 336 ACSR | 12.0956 | 529.0454 | 540 | 97.97% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 380000 | 0 | 0 | 445660.9856 |  |  | 1053660.9856
Wilson | 13242 | RelayMicroProcessor | 13242-75054383 | 840 | 307 | 533 | 2.9169 | 3 | 2 | Knights | 13807 | RelayMicroProcessor | 10635213 | 161 | PCA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 6.0354 | 0 | 0 | 77.64% | 336 ACSR | 419.2357 | 77.64% | 336 ACSR | 9.585 | 419.2357 | 540 | 0.77636 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 152000 | 0 | 0 | 0 |  |  | 380000
Dade City N | 13331 | RelayMicroProcessor | 13331-75501709 | 1530 | 454 | 1076 | 3.0383 | 3 | 4 | Blanton | 13813 | RelayMicroProcessor | 13331-92635783 | 20 | DCA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 20.0373 | 0 | 0 | 100.8% | 2/0 AAAC | 312.5911 | 83.37% | 2/0 AAAC | 5.9086 | 258.4346 | 310 | 0.83366 | 0.14527 | Yes | 0.14527 | 0 | 0 | Group 2:Requires conductor upgrades | 228000 | 0 | 304000 | 41323.659 | 0 | 0 |  |  | 573323.659
Dade City N | 13330 | RelayMicroProcessor | 13330-72400577 | 2009 | 433 | 1576 | 5.1591 | 3 | 5 | Blanton | 13815 | RelayMicroProcessor | 10745761 | 50 | DCA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 20.0373 | 0.754 | 32.9789 | 120.4% | 2 AAAC | 240.8413 | 88.59% | 2/0 AAAC | 6.279 | 274.6345 | 310 | 0.9923 | 0.2089 | Yes | 0.2089 | 0 | 0 | Group 2:Requires conductor upgrades | 228000 | 0 | 380000 | 59426.331 | 0 | 0 |  |  | 667426.331
Gulf City | 13256 | RelayMicroProcessor | 13256-74856023 | 1070 | 300 | 770 | 2.0273 | 3 | 3 | Ruskin E | 13817 | RelayElectromechanical | 13256-93118770 | 112 | SHA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 18.0369 | 0 | 0 | 65.02% | 336 ACSR | 351.1044 | 65.02% | 336 ACSR | 8.0273 | 351.1044 | 540 | 0.65019 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 228000 | 0 | 0 | 0 |  |  | 576000
Ruskin E | 13818 | RelayMicroProcessor | 13818-75559366 | 977 | 455 | 522 | 2.2057 | 3 | 2 | Ruskin W | 13819 | RelayMicroProcessor | 93507609 | 123 | SHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 11.4661 | 3.75 | 164.02 | 61.91% | 1/0 ALCN | 102.1544 | 61.91% | 1/0 ALCN | 2.3356 | 102.1544 | 165 | 1.6132 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 152000 | 0 | 0 | 0 |  |  | 380000
Fowler E | 13829 | RelayElectromechanical | 13829-75703358 | 855 | 298 | 557 | 2.8927 | 3 | 2 | Fowler W | 13826 | RelayMicroProcessor | 60127689 | 160 | CSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 4.499 | 0 | 0 | 70.23% | 336 ACSR | 379.2596 | 70.23% | 336 ACSR | 8.671 | 379.2596 | 540 | 0.70233 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 152000 | 0 | 0 | 0 |  |  | 500000
Harney Rd East | 14040 | RelayMicroProcessor | 14040-90668033 | 1892 | 309 | 1583 | 5.6198 | 3 | 5 | Fowler W | 13826 | RelayMicroProcessor | 60211585 | 41 | CSA | 4 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 4.499 | 0 | 0 | 97.79% | 336 ACSR | 528.0605 | 97.79% | 336 ACSR | 12.0731 | 528.0605 | 540 | 97.79% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 380000 | 0 | 0 | 445660.9856 |  |  | 1053660.9856
Fowler W | 13827 | RelayElectromechanical | 13827-10423128 | 779 | 225 | 554 | 3.2723 | 3 | 2 | Fowler E | 13830 | RelayMicroProcessor | 13827-92759884 | 217 | CSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 12.7213 | 0 | 0 | 207% | 1/0 ALCN | 341.5015 | 65.53% | 1/0 ALCN | 2.4722 | 108.1323 | 165 | 0.65535 | 0.20511 | Yes | 0 | 0 | 0.20511 | Group 2:Requires conductor upgrades | 228000 | 120000 | 152000 | 66203.2977 | 0 | 0 |  |  | 566203.2977
Pine Lake S | 13630 | RelayMicroProcessor | 13630-75500342 | 1200 | 307 | 893 | 4.889 | 3 | 3 | Florida Ave S | 13835 | RelayMicroProcessor | 60344887 | 236 | CSA | 5 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 5.2878 | 0 | 0 | 89.01% | 336 ACSR | 480.6393 | 89.01% | 336 ACSR | 10.9889 | 480.6393 | 540 | 0.89007 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 228000 | 0 | 0 | 0 |  |  | 456000
Lk Magdalene N | 13935 | RelayElectromechanical | 13935-73005500 | 675 | 303 | 372 | 1.6299 | 3 | 2 | Florida Ave N | 13836 | RelayMicroProcessor | 10429859 | 246 | CSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 8.4224 | 0 | 0 | 62.48% | 336 ACSR | 337.3952 | 62.48% | 336 ACSR | 7.7139 | 337.3952 | 540 | 0.62481 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 152000 | 0 | 0 | 0 |  |  | 500000
27th St N | 13351 | RelayMicroProcessor | 13351-75559990 | 1898 | 386 | 1512 | 4.4272 | 3 | 5 | Florida Ave S | 13838 | RelayMicroProcessor | 13351-93281369 | 12 | CSA | 4 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 5.2878 | 0 | 0 | 92.6% | 336 ACSR | 500.0444 | 92.6% | 336 ACSR | 11.4326 | 500.0445 | 540 | 92.6% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 380000 | 0 | 0 | 445660.9856 |  |  | 1053660.9856
McFarland | 13107 | RelayMicroProcessor | 13107-75805587 | 1772 | 269 | 1503 | 5.6341 | 3 | 5 | Florida Ave S | 13838 | RelayMicroProcessor | 91354615 | 89 | CSA | 2 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 5.2878 | 0 | 0 | 112.2% | 2 AAAC | 224.4662 | 99.93% | 336 ACSR | 12.338 | 539.6466 | 540 | 99.93% | 0.016667 | No | 0.016667 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 380000 | 4741.176 | 0 | 445660.9856 |  |  | 1058402.1616
Sunset Lane E | 13993 | RelayMicroProcessor | 60118654 | 1218 | 309 | 909 | 4.4747 | 3 | 3 | Florida Ave S | 13839 | RelayMicroProcessor | 60555876 | 144 | CSA | 4 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 5.2878 | 0 | 0 | 114.7% | SGBUS | 645.809 | 114.7% | SGBUS | 14.7652 | 645.809 | 563 | 114.7% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 228000 | 0 | 0 | 445660.9856 |  |  | 901660.9856
Florida Ave S | 13838 | RelayMicroProcessor | 13838-74310880 | 1930 | 321 | 1609 | 4.8033 | 3 | 5 | Florida Ave N | 13840 | RelayMicroProcessor | 93024657 | 45 | CSA | 5 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 8.4224 | 0 | 0 | 168.9% | 2/0 AAAC | 523.546 | 96.95% | 336 ACSR | 11.9689 | 523.5034 | 540 | 96.95% | 0.033333 | No | 0.033333 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 380000 | 9482.352 | 0 | 445660.9856 |  |  | 1063143.3376
Sunset Lane E | 13097 | RelayMicroProcessor | 13097-74311054 | 1503 | 223 | 1280 | 6.3812 | 3 | 4 | Florida Ave N | 13840 | RelayMicroProcessor | 93013058 | 227 | CSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 8.4224 | 0 | 0 | 189% | 2/0 AAAC | 585.9836 | 108.5% | 336 ACSR | 13.3972 | 585.9746 | 540 | 108.5% | 0.0073864 | No | 0.0073864 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 304000 | 2101.203 | 0 | 445660.9856 |  |  | 979762.1886
Seneca N | 13590 | RelayMicroProcessor | 13590-10396567 | 1706 | 420 | 1286 | 4.7317 | 3 | 4 | McKinley W | 13844 | RelayMicroProcessor | 91459862 | 66 | CSA | 5 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 19.787 | 2.2 | 96.225 | 113.6% | 2 AAAC | 227.2406 | 90.32% | 336 ACSR | 11.1513 | 487.7438 | 540 | 108.1% | 0.0096591 | No | 0.0096591 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 304000 | 2747.727 | 0 | 445660.9856 |  |  | 980408.7126
Mulberry W | 13010 | RelayMicroProcessor | 13010-90666359 | 1768 | 450 | 1318 | 4.5116 | 3 | 4 | Imperial Lakes | 13853 | RelayMicroProcessor | 13010-92956889 | 64 | PCA | 1 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 3.8223 | 0 | 0 | 103.6% | SGBUS | 583.1239 | 103.6% | SGBUS | 13.332 | 583.1239 | 563 | 103.6% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 304000 | 0 | 0 | 445660.9856 |  |  | 977660.9856
Hopewell | 13147 | RelayElectromechanical | 13147-76003621 | 1804 | 238 | 1566 | 6.2906 | 3 | 5 | Imperial Lakes | 13854 | RelayMicroProcessor | 13147-92872006 | 139 | PCA | 4 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 3.8223 | 0 | 0 | 124.2% | 336 ACSR | 670.4986 | 124.2% | 336 ACSR | 15.3297 | 670.4986 | 540 | 124.2% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 380000 | 0 | 0 | 445660.9856 |  |  | 1173660.9856
ROCKY_CR S | 13428 | RelayMicroProcessor | 13428-90600253 | 1315 | 367 | 948 | 3.6922 | 3 | 3 | PATSN_RD W | 13860 | RelayElectromechanical | 10213741 | 103 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 6.104 | 0 | 0 | 101% | 4/0 AAAC | 414.0255 | 76.96% | 336 ACSR | 9.5013 | 415.5729 | 540 | 0.76958 | 0.045644 | Yes | 0.045644 | 0 | 0 | Group 2:Requires conductor upgrades | 228000 | 120000 | 228000 | 12984.357 | 0 | 0 |  |  | 588984.357
GEORG_RD N | 13516 | RelayElectromechanical | 13516-74200843 | 954 | 394 | 560 | 3.4836 | 3 | 2 | PATSN_RD W | 13864 | RelayMicroProcessor | 10310574 | 182 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 6.104 | 0 | 0 | 81.21% | 336 ACSR | 438.5559 | 81.21% | 336 ACSR | 10.0267 | 438.5559 | 540 | 0.81214 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 152000 | 0 | 0 | 0 |  |  | 500000
ROCKY_CR N | 13574 | RelayElectromechanical | 13574-60095133 | 890 | 353 | 537 | 2.8641 | 3 | 2 | PATSN_RD E | 13865 | RelayElectromechanical | 60134793 | 157 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 5.6399 | 0 | 0 | 117.1% | 2 AAAC | 234.1491 | 97.94% | 1000 ALJCN | 12.3829 | 541.6093 | 553 | 97.94% | 0.027462 | No | 0.027462 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 240000 | 152000 | 7812.165 | 0 | 445660.9856 |  |  | 1073473.1506
ROCKY_CR N | 13572 | RelayElectromechanical | 13572-92511033 | 1029 | 252 | 777 | 2.9575 | 3 | 3 | PATSN_RD E | 13865 | RelayElectromechanical | 60146512 | 121 | WSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 5.6399 | 0 | 0 | 96.13% | 1000 ALJCN | 531.6257 | 96.13% | 1000 ALJCN | 12.1546 | 531.6255 | 553 | 96.13% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 240000 | 228000 | 0 | 0 | 445660.9856 |  |  | 1141660.9856
CASEY_RD S | 13750 | RelayMicroProcessor | 13750-74751764 | 715 | 339 | 376 | 1.6722 | 3 | 2 | PATSN_RD E | 13866 | RelayElectromechanical | 10313842 | 260 | WSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 5.6399 | 0 | 0 | 145.6% | 1/0 ALCN | 240.2703 | 77.82% | 336 ACSR | 9.608 | 420.2404 | 540 | 0.77822 | 0.047917 | Yes | 0 | 0 | 0.047917 | Group 2:Requires conductor upgrades | 228000 | 120000 | 152000 | 15465.775 | 0 | 0 |  |  | 515465.775
HENDERSN E | 13871 | RelayMicroProcessor | 13871-74650322 | 995 | 419 | 576 | 2.035 | 3 | 2 | PATSN_RD E | 13866 | RelayElectromechanical | 10313841 | 133 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 5.6399 | 0 | 0 | 153% | 1/0 ALCN | 252.391 | 77.9% | 336 ACSR | 9.617 | 420.6337 | 540 | 0.77895 | 0.047917 | Yes | 0 | 0 | 0.047917 | Group 2:Requires conductor upgrades | 228000 | 120000 | 152000 | 15465.775 | 0 | 0 |  |  | 515465.775
HENDERSN E | 13870 | RelayMicroProcessor | 13870-75650144 | 1875 | 477 | 1398 | 6.3253 | 3 | 4 | PATSN_RD E | 13869 | RelayElectromechanical | 91675885 | 118 | WSA | 3 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 5.6399 | 0 | 0 | 223% | 1/0 ALCN | 367.9415 | 97.31% | 336 ACSR | 12.0141 | 525.481 | 540 | 97.31% | 0.19811 | No | 0.11004 | 0 | 0.088068 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 304000 | 59727.7756 | 0 | 445660.9856 |  |  | 1157388.7612
CARROLWD W | 13544 | RelayMicroProcessor | 13544-74318006 | 747 | 321 | 426 | 1.8752 | 3 | 2 | HENDERSN E | 13870 | RelayMicroProcessor | 60111904 | 183 | WSA | 1 | Adjacent XFM loaded over 100% | HENDERSN E transformer upgrade | 28 | -4.1259 | 4.1 | 179.3285 | 81.91% | 336 ACSR | 442.3211 | 81.91% | 336 ACSR | 10.1128 | 442.3212 | 540 | 1.1512 | 0 | No | 0 | 0 | 0 | Group 3: Requires transformer upgrade | 228000 | 0 | 152000 | 0 | 1750000 | 0 |  |  | 2130000
HENDERSN E | 13873 | RelayMicroProcessor | 13873-74650267 | 1457 | 479 | 978 | 4.367 | 3 | 3 | HENDERSN E | 13870 | RelayMicroProcessor | 13870-60111963 | 271 | WSA | 2 | Adjacent XFM loaded over 100% | HENDERSN E transformer upgrade | 28 | -4.1259 | 4.1 | 179.3285 | 96.72% | 336 ACSR | 522.2694 | 96.72% | 336 ACSR | 11.9407 | 522.2695 | 540 | 129.9% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 228000 | 0 | 1750000 | 445660.9856 |  |  | 2651660.9856
Brandon W | 13230 | RelayMicroProcessor | 13230-76103514 | 1251 | 344 | 907 | 3.7926 | 3 | 3 | Providence E | 13878 | RelayMicroProcessor | 60380906 | 99 | ESA | 3 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 2.2676 | 0 | 0 | 139.9% | 1/0 ALCN | 230.8931 | 90.78% | 336 ACSR | 11.2074 | 490.1978 | 540 | 90.78% | 0.35114 | No | 0.026705 | 0 | 0.32443 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 228000 | 112311.5684 | 0 | 445660.9856 |  |  | 1013972.554
Providence W | 13884 | RelayMicroProcessor | 13884-60153115 | 1634 | 315 | 1319 | 5.1179 | 3 | 4 | Providence E | 13878 | RelayMicroProcessor | 60179185 | 188 | ESA | 4 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 2.2676 | 0 | 0 | 101.6% | 336 ACSR | 548.3748 | 101.6% | 336 ACSR | 12.5375 | 548.3746 | 540 | 101.6% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 304000 | 0 | 0 | 445660.9856 |  |  | 977660.9856
Providence E | 13880 | RelayElectromechanical | 13880-76104695 | 1686 | 406 | 1280 | 6.0196 | 3 | 4 | Providence E | 13879 | RelayElectromechanical | 60533215 | 159 | ESA | 3 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 2.2676 | 0 | 0 | 109.2% | 336 ACSR | 589.7228 | 109.2% | 336 ACSR | 13.4829 | 589.7232 | 540 | 109.2% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 240000 | 304000 | 0 | 0 | 445660.9856 |  |  | 1217660.9856
Buckhorn N | 13707 | RelayMicroProcessor | 13707-10847671 | 1181 | 444 | 737 | 2.8714 | 3 | 3 | Providence W | 13885 | RelayMicroProcessor | 10108300 | 211 | ESA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 13.3733 | 0 | 0 | 124.5% | 2/0 AAAC | 386.0906 | 72.92% | 336 ACSR | 9.0032 | 393.7884 | 540 | 0.72924 | 0.24034 | Yes | 0.24034 | 1 | 0 | Group 2:Requires conductor upgrades | 228000 | 0 | 228000 | 80772.913 | 0 | 0 |  |  | 536772.913
CARROLWD E | 13538 | RelayElectromechanical | 13538-75050593 | 946 | 290 | 656 | 5.2642 | 3 | 2 | EHRLICH W | 13886 | RelayElectromechanical | 60120746 | 295 | WSA | 2 | Adjacent XFM loaded over 100% | EHRLICH W transformer upgrade | 28 | 3.8657 | 0 | 0 | 160.3% | 1/0 ALCN | 264.4304 | 84.72% | 1000 ALJCN | 10.7115 | 468.5079 | 553 | 0.84721 | 0.85966 | Yes | 0 | 0 | 0.85966 | Group 3: Requires transformer upgrade | 228000 | 240000 | 152000 | 277467.0068 | 1750000 | 0 |  |  | 2647467.0068
D_MABRY W | 13584 | RelayMicroProcessor | 13584-74751687 | 953 | 326 | 627 | 2.7604 | 3 | 2 | EHRLICH W | 13888 | RelayElectromechanical | 60055763 | 191 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 3.8657 | 0 | 0 | 151.8% | 2 AAAC | 303.6254 | 70.2% | 336 ACSR | 8.6669 | 379.0772 | 540 | 0.70199 | 0.00018939 | Yes | 0.00018939 | 0 | 0 | Group 2:Requires conductor upgrades | 228000 | 120000 | 152000 | 53.877 | 0 | 0 |  |  | 500053.877
CARROLWD W | 13540 | RelayElectromechanical | 13540-75056868 | 722 | 286 | 436 | 1.4019 | 3 | 2 | EHRLICH W | 13889 | RelayMicroProcessor | 93646283 | 252 | WSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 3.8657 | 0 | 0 | 99.44% | 336 ACSR | 536.9863 | 99.44% | 336 ACSR | 12.2772 | 536.9863 | 540 | 99.44% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 152000 | 0 | 0 | 445660.9856 |  |  | 945660.9856
HENDERSN E | 13872 | RelayMicroProcessor | 91280901 | 930 | 328 | 602 | 2.4171 | 3 | 2 | EHRLICH W | 13889 | RelayMicroProcessor | 10328337 | 168 | WSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 3.8657 | 0 | 0 | 110.2% | 336 ACSR | 595.0095 | 110.2% | 336 ACSR | 13.6037 | 595.0095 | 540 | 110.2% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 152000 | 0 | 0 | 445660.9856 |  |  | 825660.9856
D_MABRY W | 13585 | RelayMicroProcessor | 13585-60099344 | 1436 | 303 | 1133 | 5.5362 | 3 | 4 | EHRLICH E | 13891 | RelayMicroProcessor | 92696158 | 101 | WSA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 8.0474 | 0 | 0 | 181.6% | 4/0 ALJCN | 414.0157 | 95.92% | 336 ACSR | 11.8424 | 517.9704 | 540 | 95.92% | 0.47008 | No | 0 | 0 | 0.47008 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 304000 | 151723.5318 | 0 | 445660.9856 |  |  | 1129384.5174
First Street S | 13896 | RelayMicroProcessor | 13896-75808599 | 2123 | 395 | 1728 | 3.9873 | 3 | 5 | First Street N | 13897 | RelayMicroProcessor | 93456651 | 10 | SHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 10.9355 | 0.754 | 32.9789 | 68.04% | 336 ACSR | 367.4299 | 68.04% | 336 ACSR | 8.4006 | 367.4299 | 540 | 0.7415 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 380000 | 0 | 0 | 0 |  |  | 608000
Peach W | 13910 | RelayElectromechanical | 13910-73506494 | 1368 | 318 | 1050 | 4.5492 | 3 | 3 | Peach W | 13906 | RelayElectromechanical | 10546227 | 54 | ESA | 2 | Adjacent XFM loaded over 100% | Peach W transformer upgrade | 28 | 1.0902 | 0 | 0 | 99.75% | 336 ACSR | 538.6367 | 99.75% | 336 ACSR | 12.3149 | 538.6367 | 540 | 99.75% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 240000 | 228000 | 0 | 1750000 | 445660.9856 |  |  | 2891660.9856
Peach W | 13906 | RelayElectromechanical | 13906-73506625 | 1769 | 330 | 1439 | 5.1092 | 3 | 5 | Peach W | 13910 | RelayElectromechanical | 10546227 | 122 | ESA | 3 | Adjacent XFM loaded over 100% | Peach W transformer upgrade | 28 | 1.0902 | 0 | 0 | 88.25% | 336 ACSR | 476.5487 | 88.25% | 336 ACSR | 10.8954 | 476.5496 | 540 | 0.8825 | 0 | No | 0 | 0 | 0 | Group 3: Requires transformer upgrade | 228000 | 240000 | 380000 | 0 | 1750000 | 0 |  |  | 2598000
Lake Ruby North | 13921 | RelayMicroProcessor | 13921-10609435 | 805 | 291 | 514 | 1.7565 | 3 | 2 | Lake Ruby South | 13916 | RelayMicroProcessor | 60561948 | 173 | WHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 15.2058 | 0 | 0 | 64.79% | 336 ACSR | 349.8412 | 64.79% | 336 ACSR | 7.9984 | 349.8412 | 540 | 0.64785 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 152000 | 0 | 0 | 0 |  |  | 380000
Lake Juliana | 13769 | RelayElectromechanical | 13769-74754278 | 1951 | 331 | 1620 | 5.7717 | 3 | 5 | Lake Gum | 13924 | RelayElectromechanical | 91230241 | 21 | WHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 22.4 | 13.3338 | 0.754 | 32.9789 | 108.8% | 2 AAAC | 217.6144 | 91.48% | 336 ACSR | 11.2936 | 493.9663 | 540 | 97.58% | 0.074811 | No | 0.074811 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 240000 | 380000 | 21281.415 | 0 | 445660.9856 |  |  | 1314942.4006
Lake Alfred | 13115 | RelayElectromechanical | 13115-73210816 | 800 | 253 | 547 | 3.6069 | 3 | 2 | Lake Gum | 13927 | RelayElectromechanical | 5009304 | 242 | WHA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 22.4 | 13.3338 | 0 | 0 | 95.62% | 336 ACSR | 516.3497 | 95.62% | 336 ACSR | 11.8053 | 516.3484 | 540 | 95.62% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 240000 | 152000 | 0 | 0 | 445660.9856 |  |  | 1065660.9856
Lucerne Park | 13973 | RelayMicroProcessor | 13973-90196456 | 2354 | 383 | 1971 | 6.0444 | 3 | 6 | Lake Gum | 13927 | RelayElectromechanical | 60182079 | 43 | WHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 22.4 | 13.3338 | 0 | 0 | 123.4% | 336 ACSR | 666.5841 | 123.4% | 336 ACSR | 15.2402 | 666.5841 | 540 | 123.4% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 456000 | 0 | 0 | 445660.9856 |  |  | 1249660.9856
Pine Lake S | 13631 | RelayMicroProcessor | 13631-10409670 | 1480 | 280 | 1200 | 5.7508 | 3 | 4 | Lk Magdalene N | 13935 | RelayElectromechanical | 13631-92971526 | 100 | CSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 7.9902 | 0 | 0 | 81.61% | 336 ACSR | 440.682 | 81.61% | 336 ACSR | 10.0753 | 440.6821 | 540 | 0.81608 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 304000 | 0 | 0 | 0 |  |  | 652000
Temple Terrace S | 13204 | RelayElectromechanical | 13204-75702059 | 1905 | 403 | 1502 | 3.0784 | 3 | 5 | Yukon N | 13948 | RelayElectromechanical | 90297050 | 3 | CSA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 22.4 | 6.517 | 0 | 0 | 193.2% | 2 AAAC | 386.367 | 81.19% | 336 ACSR | 10.0238 | 438.4262 | 540 | 0.8119 | 0.35909 | Yes | 0.35909 | 0 | 0 | Group 2:Requires conductor upgrades | 228000 | 240000 | 380000 | 102150.792 | 0 | 0 |  |  | 950150.792
Lakewood S | 13454 | RelayMicroProcessor | 13454-75358734 | 1717 | 395 | 1322 | 6.5579 | 3 | 4 | SR 60 S | 13953 | RelayMicroProcessor | 10804993 | 120 | ESA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 12.3159 | 0 | 0 | 208.6% | 2 AAAC | 417.2693 | 123% | 336 ACSR | 15.1803 | 663.967 | 540 | 123% | 0.90833 | No | 0.68163 | 0 | 0.2267 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 304000 | 267075.3889 | 0 | 445660.9856 |  |  | 1244736.3745
Causeway (2018) | 14356 | RelayMicroProcessor | 60460303 | 1766 | 398 | 1368 | 6.667 | 3 | 4 | SR 60 S | 13956 | RelayMicroProcessor | 91051212 | 254 | ESA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 12.3159 | 0 | 0 | 88.08% | 336 ACSR | 475.6523 | 88.08% | 336 ACSR | 10.8749 | 475.6525 | 540 | 0.88084 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 304000 | 0 | 0 | 0 |  |  | 532000
Trout Creek N | 13986 | RelayMicroProcessor | 13986-75653416 | 987 | 236 | 751 | 3.504 | 3 | 3 | Trout Creek S | 13988 | RelayMicroProcessor | 60145648 | 288 | CSA | 2 | Adjacent XFM loaded over 100% | Trout Creek S transformer upgrade | 28 | -1.5688 | 0 | 0 | 87% | 1000 ALJCN | 481.0924 | 87% | 1000 ALJCN | 10.9993 | 481.0925 | 553 | 0.86997 | 0 | No | 0 | 0 | 0 | Group 3: Requires transformer upgrade | 228000 | 0 | 228000 | 0 | 1750000 | 0 |  |  | 2206000
Trout Creek N | 13987 | RelayMicroProcessor | 13987-75653549 | 973 | 271 | 702 | 2.242 | 3 | 3 | Trout Creek S | 13988 | RelayMicroProcessor | 93804044 | 187 | CSA | 1 | Adjacent XFM loaded over 100% | Trout Creek S transformer upgrade | 28 | -1.5688 | 0 | 0 | 74.7% | 1000 ALJCN | 413.0855 | 74.7% | 1000 ALJCN | 9.4444 | 413.0857 | 553 | 0.74699 | 0 | No | 0 | 0 | 0 | Group 3: Requires transformer upgrade | 228000 | 0 | 228000 | 0 | 1750000 | 0 |  |  | 2206000
Sunset Lane W | 13099 | RelayMicroProcessor | 13099-74311183 | 1311 | 320 | 991 | 6.0333 | 3 | 3 | Trout Creek N | 13991 | RelayMicroProcessor | 10884173 | 244 | CSA | 1 | Adjacent XFM loaded over 100% | Trout Creek N transformer upgrade | 28 | -2.305 | 0 | 0 | 144.1% | 336 ACSR | 778.3607 | 144.1% | 336 ACSR | 17.7956 | 778.3548 | 540 | 144.1% | 0.0060606 | No | 0.0060606 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 228000 | 1724.064 | 1750000 | 445660.9856 |  |  | 2653385.0496
Florida Ave S | 13839 | RelayMicroProcessor | 13839-74310524 | 1265 | 301 | 964 | 5.4331 | 3 | 3 | Sunset Lane E | 13993 | RelayMicroProcessor | 60555876 | 11 | CSA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 12.6411 | 0 | 0 | 108.1% | 336 ACSR | 583.9103 | 108.1% | 336 ACSR | 13.3499 | 583.9076 | 540 | 108.1% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 228000 | 0 | 0 | 445660.9856 |  |  | 901660.9856
Tampa Palms W | 13716 | RelayMicroProcessor | 13716-73507073 | 640 | 300 | 340 | 2.3366 | 3 | 1 | GTE-Collier N | 14011 | RelayMicroProcessor | 93391876 | 274 | CSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 9.3328 | 0.8 | 34.9909 | 124.9% | 2 AAAC | 249.8997 | 91.93% | 336 ACSR | 11.35 | 496.433 | 540 | 98.41% | 0.0047348 | No | 0.0047348 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 76000 | 1346.925 | 0 | 445660.9856 |  |  | 751007.9106
Gibsonton | 13019 | RelayMicroProcessor | 13019-74757321 | 1707 | 342 | 1365 | 7.4795 | 3 | 4 | Riverview N | 14020 | RelayMicroProcessor | 13019-93052203 | 231 | SHA | 1 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 3.0152 | 0 | 0 | 161.6% | 336 ACSR | 872.4275 | 161.5% | 336 ACSR | 19.945 | 872.3681 | 540 | 161.5% | 0.038447 | No | 0.038447 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 304000 | 10937.031 | 0 | 445660.9856 |  |  | 988598.0166
Riverview S | 14024 | RelayMicroProcessor | 14024-90118381 | 2083 | 244 | 1839 | 7.9345 | 3 | 6 | Riverview N | 14021 | RelaySolidState | 90095026 | 169 | SHA | 1 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 3.0152 | 0 | 0 | 119.2% | 336 ACSR | 643.8957 | 119.2% | 336 ACSR | 14.7213 | 643.8904 | 540 | 119.2% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 456000 | 0 | 0 | 445660.9856 |  |  | 1129660.9856
Rhodine North | 13649 | RelayMicroProcessor | 13649-76155721 | 658 | 334 | 324 | 1.2956 | 3 | 1 | Riverview S | 14023 | RelayMicroProcessor | 60268838 | 206 | SHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 5.0343 | 0.25 | 10.9347 | 58.59% | 336 ACSR | 316.411 | 58.59% | 336 ACSR | 7.2341 | 316.411 | 540 | 0.6062 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 76000 | 0 | 0 | 0 |  |  | 304000
Riverview N | 14021 | RelaySolidState | 14021-75706745 | 1201 | 342 | 859 | 4.5737 | 3 | 3 | Riverview S | 14024 | RelayMicroProcessor | 90095026 | 198 | SHA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 5.0343 | 0 | 0 | 113.8% | 336 ACSR | 614.6287 | 113.8% | 336 ACSR | 14.0518 | 614.6047 | 540 | 113.8% | 0.041856 | No | 0.041856 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 228000 | 11906.817 | 0 | 445660.9856 |  |  | 913567.8026
Riverview N | 14022 | RelayMicroProcessor | 14022-90542551 | 904 | 302 | 602 | 3.8111 | 3 | 2 | Riverview S | 14026 | RelayMicroProcessor | 92723267 | 239 | SHA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37 | 5.0343 | 0 | 0 | 55.67% | 336 ACSR | 300.5937 | 55.67% | 336 ACSR | 6.8725 | 300.5938 | 540 | 0.55666 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 152000 | 0 | 0 | 0 |  |  | 380000
Temple Terrace N | 13028 | RelayMicroProcessor | 13028-75702432 | 2066 | 316 | 1750 | 3.6892 | 3 | 5 | Harney Rd East | 14040 | RelayMicroProcessor | 13028-93596029 | 16 | CSA | 1 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 1.1245 | 0 | 0 | 84.98% | 336 ACSR | 458.917 | 84.98% | 336 ACSR | 10.4922 | 458.9168 | 540 | 0.84985 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 380000 | 0 | 0 | 0 |  |  | 608000
ROCKY_CR S | 13425 | RelayMicroProcessor | 13425-74402782 | 1694 | 360 | 1334 | 5.7519 | 3 | 4 | WSTCHASE W (230kV) | 14083 | RelayMicroProcessor | 92950259 | 116 | WSA | 4 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.33 | 12.9031 | 0 | 0 | 121.5% | 336 ACSR | 656.1619 | 121.5% | 336 ACSR | 15.0019 | 656.1623 | 540 | 121.5% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 304000 | 0 | 0 | 445660.9856 |  |  | 977660.9856
WSTCHASE W (230kV) | 14082 | RelayMicroProcessor | 93419680 | 1022 | 352 | 670 | 3.9017 | 3 | 2 | WSTCHASE W (230kV) | 14083 | RelayMicroProcessor | 60138714 | 234 | WSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.33 | 12.9031 | 0 | 0 | 101.9% | 336 ACSR | 550.3589 | 101.9% | 336 ACSR | 12.5829 | 550.3589 | 540 | 101.9% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 152000 | 0 | 0 | 445660.9856 |  |  | 825660.9856
SILVER $ | 14275 | #N/A | 14275-92878595 | 1307 | 315 | 992 | 5.7538 | 3 | 3 | WSTCHASE W (230kV) | 14084 | RelayMicroProcessor | 60240437 | 275 | WSA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.33 | 12.9031 | 0 | 0 | 183.5% | 1/0 ALCN | 302.7595 | 129.3% | 1000 ALJCN | 16.3506 | 715.1552 | 553 | 129.3% | 0.13277 | No | 0 | 0 | 0.13277 | Group 4: Requires multiple FLISR ties | 228000 | 120000 | 228000 | 42851.8114 | 0 | 445660.9856 |  |  | 1064512.797
Pebble Creek N | 14095 | RelayMicroProcessor | 14095-92240377 | 1184 | 374 | 810 | 3.8377 | 3 | 3 | Pebble Creek N | 14094 | RelayMicroProcessor | 92553975 | 230 | CSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 6.2526 | 0 | 0 | 96.91% | 336 ACSR | 523.335 | 96.88% | 336 ACSR | 11.9606 | 523.1416 | 540 | 96.88% | 0.35985 | No | 0 | 0 | 0.35985 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 228000 | 116146.1364 | 0 | 445660.9856 |  |  | 1017807.122
Pebble Creek S | 14092 | RelayMicroProcessor | 14092-90033546 | 1499 | 379 | 1120 | 0.6117 | 3 | 4 | Pebble Creek N | 14096 | RelayMicroProcessor | 93522876 | 2 | CSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 6.2526 | 0 | 0 | 55.35% | 336 ACSR | 298.8718 | 55.35% | 336 ACSR | 6.8331 | 298.8721 | 540 | 0.55347 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 304000 | 0 | 0 | 0 |  |  | 532000
Cross Creek W | 14101 | RelayMicroProcessor | 60232041 | 1547 | 438 | 1109 | 5.7004 | 3 | 4 | Cross Creek W | 14099 | RelayMicroProcessor | 93438050 | 70 | CSA | 5 | Adjacent XFM loaded over 100% | Cross Creek W transformer upgrade | 28 | 4.3344 | 0 | 0 | 89.17% | 336 ACSR | 481.4912 | 89.17% | 336 ACSR | 11.0084 | 481.4912 | 540 | 0.89165 | 0 | No | 0 | 0 | 0 | Group 3: Requires transformer upgrade | 228000 | 0 | 304000 | 0 | 1750000 | 0 |  |  | 2282000
Pebble Creek N | 14096 | RelayMicroProcessor | 90575476 | 1333 | 273 | 1060 | 4.2677 | 3 | 4 | Cross Creek W | 14101 | RelayMicroProcessor | 93004122 | 154 | CSA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 4.3344 | 0 | 0 | 100.3% | SGBUS | 564.6999 | 100.3% | SGBUS | 12.9108 | 564.6999 | 563 | 100.3% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 304000 | 0 | 0 | 445660.9856 |  |  | 977660.9856
Cross Creek W | 14099 | RelayMicroProcessor | 91668167 | 756 | 343 | 413 | 2.8476 | 3 | 2 | Cross Creek E | 14102 | RelayMicroProcessor | 93018699 | 293 | CSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 17.499 | 0 | 0 | 106.7% | 336 ACSR | 576.2709 | 106.7% | 336 ACSR | 13.1753 | 576.2709 | 540 | 106.7% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 152000 | 0 | 0 | 445660.9856 |  |  | 825660.9856
Bell Shoals | 13731 | RelayMicroProcessor | 13731-93642814 | 898 | 485 | 413 | 1.9887 | 3 | 2 | Bloomingdale N | 14110 | RelayMicroProcessor | 92888727 | 167 | ESA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 2.9924 | 0 | 0 | 73.89% | 336 ACSR | 399.0247 | 73.89% | 336 ACSR | 9.1229 | 399.0247 | 540 | 0.73893 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 152000 | 0 | 0 | 0 |  |  | 380000
Buckhorn N | 13705 | RelayMicroProcessor | 13705-10533429 | 1624 | 271 | 1353 | 5.9933 | 3 | 4 | Bloomingdale N | 14110 | RelayMicroProcessor | 60504829 | 143 | ESA | 1 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 2.9924 | 0 | 0 | 170.4% | 1/0 ALCN | 281.0894 | 110.9% | 336 ACSR | 13.689 | 598.7378 | 540 | 110.9% | 0.20587 | No | 0 | 0 | 0.20587 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 304000 | 66447.8159 | 0 | 445660.9856 |  |  | 1044108.8015
Providence W | 13883 | RelayElectromechanical | 13883-92896754 | 1443 | 255 | 1188 | 3.6042 | 3 | 4 | Lakewood N | 14115 | RelayMicroProcessor | 60142918 | 148 | ESA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 16.7964 | 0 | 0 | 78.97% | 336 ACSR | 426.4111 | 78.97% | 336 ACSR | 9.7491 | 426.4111 | 540 | 0.78965 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 120000 | 304000 | 0 | 0 | 0 |  |  | 652000
Brandon W | 13228 | RelayMicroProcessor | 13228-60318155 | 1185 | 289 | 896 | 4.243 | 3 | 3 | Lakewood N | 14116 | RelayMicroProcessor | 60145098 | 218 | ESA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 37.3 | 16.7964 | 0 | 0 | 69.63% | 336 ACSR | 376.0073 | 69.63% | 336 ACSR | 8.5967 | 376.0075 | 540 | 0.69631 | 0 | No | 0 | 0 | 0 | Group 1: Recloser Install / breaker replacement | 228000 | 0 | 228000 | 0 | 0 | 0 |  |  | 456000
Trout Creek S | 13988 | RelayMicroProcessor | 13988-60147913 | 1303 | 390 | 913 | 4.8065 | 3 | 3 | Wilderness East | 14216 | RelayMicroProcessor | 93172233 | 164 | CSA | 3 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 19.591 | 0 | 0 | 158.2% | 1/0 ALCN | 261.082 | 103.2% | SGBUS | 13.2895 | 581.267 | 563 | 103.2% | 2.811 | No | 0 | 0 | 2.811 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 228000 | 907284.7136 | 0 | 445660.9856 |  |  | 1808945.6992
Trout Creek S | 13992 | RelayMicroProcessor | 93433111 | 1021 | 267 | 754 | 4.8703 | 3 | 3 | Wilderness East | 14218 | RelayMicroProcessor | 92334909 | 283 | CSA | 1 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 19.591 | 0 | 0 | 114.1% | 336 ACSR | 616.0785 | 114.1% | 336 ACSR | 14.0854 | 616.0785 | 540 | 114.1% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 228000 | 0 | 0 | 445660.9856 |  |  | 901660.9856
Seventy Eighth St | 13133 | RelayMicroProcessor | 13133-72703760 | 1703 | 314 | 1389 | 6.0881 | 3 | 4 | Causeway (2018) | 14355 | RelayMicroProcessor | 90092112 | 141 | ESA | 1 | Adjacent XFM loaded over 100% | No transformer upgrade | 28 | 3.6668 | 0 | 0 | 111.7% | 336 ACSR | 603.0564 | 111.7% | 336 ACSR | 13.7857 | 602.9679 | 540 | 111.7% | 0.10985 | No | 0.10985 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 304000 | 31248.66 | 0 | 445660.9856 |  |  | 1008909.6456
SR 60 S | 13956 | RelayMicroProcessor | 13956-72704776 | 772 | 336 | 436 | 2.5422 | 3 | 2 | Causeway (2018) | 14356 | RelayMicroProcessor | 60257488 | 209 | ESA | 2 | XFM has enough capacity to pick up zone 2 load | No transformer upgrade | 28 | 3.6668 | 0 | 0 | 91.09% | 336 ACSR | 491.8955 | 91.09% | 336 ACSR | 11.2462 | 491.8955 | 540 | 91.09% | 0 | No | 0 | 0 | 0 | Group 4: Requires multiple FLISR ties | 228000 | 0 | 152000 | 0 | 0 | 445660.9856 |  |  | 825660.9856

## Cost_Grouping_Charts
| Total | CSA | DCA | ESA | PCA | SHA | WHA | WSA
Group 1: Recloser Install / breaker replacement | 101 | 22 | 6 | 12 | 5 | 9 | 10 | 37
Group 2:Requires conductor upgrades | 39 | 9 | 2 | 3 | 0 | 2 | 3 | 20
Group 3: Requires transformer upgrade | 26 | 9 | 0 | 8 | 1 | 0 | 0 | 8
Group 4: Requires multiple FLISR ties | 134 | 28 | 0 | 33 | 10 | 13 | 15 | 35
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.

## Cost_Per_Feeder_Graph
Region | Total Estimated Cost | CSA | DCA | ESA | PCA | SHA | WHA | WSA | CSA | [11 empty] | 380000 | 380000 | 380000 | 380000 | [18 empty] | 399255.8068 | 424000 |  |  | 456000 | 456000 | 456000 | 456000 | [11 empty] | 500000 | 500000 | 500000 | 500000 | [18 empty] | 512528.263 |  |  | 524693.175 | 532000 | 532000 | 532000 |  |  |  |  | 538970.58 |  |  |  | 566203.2977 | [13 empty] | 608000 | [7 empty] | 652000 | 652000 | 652000 | [6 empty] | 696000 |  |  | 712809.624 | 728000 |  |  | 751007.9106 |  |  |  | 790877.397 |  | 825660.9856 | [5 empty] | 872620.872 |  | 901660.9856 | 901660.9856 | 901660.9856 | [11 empty] | 950150.792 |  |  | 977660.9856 | [7 empty] | 979762.1886 | 980408.7126 | 983695.2096 | [5 empty] | 1017807.122 | [8 empty] | 1053660.9856 | 1053660.9856 | 1053660.9856 | 1053660.9856 | [6 empty] | 1056853.0151 | 1058402.1616 | 1063143.3376 | [6 empty] | 1097660.9856 | [9 empty] | 1136791.5036 | [16 empty] | 1293532.6796 |  |  |  | 1397867.4556 | [10 empty] | 1808945.6992 |  |  | 2130000 |  |  |  | 2130053.877 |  |  |  | 2206000 | 2206000 |  |  |  | 2282000 |  |  |  | 2354626.196 |  |  | 2452857.0795 | 2462400.5943 |  |  | 2604249.732 |  |  |  | 2653385.0496 |  |  | 2682959.3129 | [9 empty] | 2913090.1524 |  |  |  | 3003655.3476 | 3031660.9856 |  | 3060976.8373
DCA | 304000 |  | 304000 | [5 empty] | DCA | 304000 | [14 empty] | 380000 | 380000 | [39 empty] | 500000 | [33 empty] | 573323.659 |  | 576000 | [26 empty] | 667426.331 | [5 empty] | 728000
ESA | 304000 |  |  | 304000 |  |  |  |  | ESA |  | 304000 | 304000 | 304000 | [13 empty] | 380000 | 380000 | 380000 | [11 empty] | 383771.39 | [9 empty] | 456000 | 456000 | 456000 | [29 empty] | 511406.003 | [7 empty] | 532000 | 532000 |  | 536772.913 | [29 empty] | 652000 | [19 empty] | 825660.9856 | [9 empty] | 901660.9856 | 901660.9856 | 901660.9856 | 901660.9856 | 901660.9856 |  |  | 905432.3756 |  |  |  |  | 952267.5666 |  |  | 977660.9856 | 977660.9856 | [8 empty] | 985096.0116 |  |  | 1008909.6456 | 1013972.554 |  | 1021660.9856 | [6 empty] | 1044108.8015 |  |  |  |  | 1053660.9856 | [15 empty] | 1097660.9856 | 1097660.9856 | [15 empty] | 1175546.6806 |  | 1215500.072 | 1217660.9856 |  |  | 1244736.3745 | [13 empty] | 1512197.8858 | [7 empty] | 2130000 | [8 empty] | 2206000 | 2217152.539 | 2250000 |  | 2282000 | 2282000 |  |  | 2370000 |  |  |  |  | 2598000 |  |  | 2651660.9856 | [5 empty] | 2694229.512 | 2695660.9856 | 2727660.9856 |  |  | 2771660.9856 |  | 2849546.6806 | 2891660.9856 |  |  |  | 2999660.9856 |  |  | 3039419.2736 |  |  |  |  | 3565380.7122
ESA | 304000 |  |  | 304000 |  |  |  |  | PCA | [20 empty] | 380000 | 380000 | [22 empty] | 456000 | [12 empty] | 500000 | [51 empty] | 620000 | [51 empty] | 977660.9856 | 977660.9856 | [8 empty] | 995239.3728 |  |  |  |  | 1021660.9856 | [11 empty] | 1053660.9856 |  |  |  | 1053714.8626 |  |  |  |  | 1065660.9856 | [18 empty] | 1173660.9856 | [32 empty] | 2130000 | [32 empty] | 2727660.9856 | [13 empty] | 3077240.7798
ESA | 304000 |  |  | 304000 |  |  |  |  | SHA |  |  |  |  | 304000 | 304000 | [16 empty] | 380000 | 380000 | [24 empty] | 456053.877 | [9 empty] | 500000 | [34 empty] | 576000 | [10 empty] | 608000 | 608862.032 | [20 empty] | 728000 | [8 empty] | 825660.9856 |  |  |  |  | 880000 | [11 empty] | 913567.8026 | [10 empty] | 977660.9856 | [6 empty] | 988598.0166 | [18 empty] | 1053660.9856 | 1053660.9856 | [14 empty] | 1097714.8626 | 1114690.6436 |  |  |  | 1129660.9856 | [17 empty] | 1281660.9856 | [6 empty] | 1412191.9736 |  |  | 1442518.2987 | [51 empty] | 2942697.0756
SHA | 304000 |  |  |  |  | 304000 |  |  | WHA | [6 empty] | 304000 | [17 empty] | 380000 | [10 empty] | 424000 | [23 empty] | 500000 | [28 empty] | 565767.896 | [5 empty] | 576000 | 576000 | [10 empty] | 611513.5636 |  |  |  | 620000 |  |  |  |  | 652000 | [5 empty] | 696000 | 696000 | [13 empty] | 825660.9856 | [16 empty] | 945660.9856 | [26 empty] | 1032544.1396 | [17 empty] | 1065660.9856 | 1065660.9856 | [7 empty] | 1120504.8336 | [9 empty] | 1173660.9856 |  |  |  | 1202180.8025 |  |  |  | 1237231.2146 |  | 1249660.9856 |  |  | 1314942.4006 | 1329969.2333 | 1335197.2146 |  | 1407438.7881 |  | 1428394.3796 | [5 empty] | 1580394.3796
SHA | 304000 |  |  |  |  | 304000 |  |  | WSA | [7 empty] | 304000 | 304000 | 304000 | 304000 | [14 empty] | 380000 | 380000 | 380000 | 380000 | 380000 | 380000 |  | 393815.2773 |  |  |  | 424000 | [8 empty] | 456000 | 456000 | 456000 |  | 456053.877 | 474494.039 | 478002.263 | [8 empty] | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500053.877 |  |  | 515465.775 | 515465.775 | [6 empty] | 532646.524 |  |  | 544000 | 561955.612 |  |  |  | 574688.653 |  |  |  |  | 576000 | 576000 | 576000 | 576000 | 576000 | 576000 | 588984.357 |  |  |  |  | 612631.7544 | 615580.0636 | [7 empty] | 652000 | 652000 | 652000 | [9 empty] | 752371.158 | 760000 | 771018.819 |  | 803781.9591 |  |  |  |  | 825660.9856 | 825660.9856 | [10 empty] | 901660.9856 | 901660.9856 |  |  |  | 945660.9856 |  |  | 967139.556 | [6 empty] | 977660.9856 | 977984.2476 | [11 empty] | 1021660.9856 | 1021660.9856 | 1021660.9856 |  | 1040661.65 | [9 empty] | 1053660.9856 |  |  |  |  | 1064512.797 |  |  |  | 1069015.9306 | 1073473.1506 | [6 empty] | 1125100.1946 | 1129384.5174 |  | 1130523.0176 |  | 1141660.9856 | 1157388.7612 | 1161617.4705 |  |  | 1173660.9856 | 1173660.9856 |  |  |  |  | 1217660.9856 | [12 empty] | 1438358.6866 |  | 1469450.8811 |  | 1529373.8106 |  | 1624491.6003 |  | 1940491.1998 | 2079141.6598 |  |  |  | 2130000 |  | 2150527.137 | 2156249.389 | 2174000 | [8 empty] | 2326000 |  |  | 2447957.081 |  |  | 2488214.108 |  |  | 2647467.0068 |  | 2651660.9856 |  | 2657102.5626 | 2664106.5726 | [5 empty] | 2727660.9856 |  | 2816106.5726 |  |  |  | 2923660.9856 | [7 empty] | 3124240.4256 | 3129214.7712
WHA | 304000 | [5 empty] | 304000
WSA | 304000 | [6 empty] | 304000
WSA | 304000 | [6 empty] | 304000
WSA | 304000 | [6 empty] | 304000
WSA | 304000 | [6 empty] | 304000
CSA | 380000 | 380000
CSA | 380000 | 380000
CSA | 380000 | 380000
CSA | 380000 | 380000
DCA | 380000 |  | 380000
DCA | 380000 |  | 380000
ESA | 380000 |  |  | 380000
ESA | 380000 |  |  | 380000
ESA | 380000 |  |  | 380000
PCA | 380000 |  |  |  | 380000
PCA | 380000 |  |  |  | 380000
SHA | 380000 |  |  |  |  | 380000
SHA | 380000 |  |  |  |  | 380000
WHA | 380000 | [5 empty] | 380000
WSA | 380000 | [6 empty] | 380000
WSA | 380000 | [6 empty] | 380000
WSA | 380000 | [6 empty] | 380000
WSA | 380000 | [6 empty] | 380000
WSA | 380000 | [6 empty] | 380000
WSA | 380000 | [6 empty] | 380000
ESA | 383771.39 |  |  | 383771.39
WSA | 393815.2773 | [6 empty] | 393815.2773
CSA | 399255.8068 | 399255.8068
CSA | 424000 | 424000
WHA | 424000 | [5 empty] | 424000
WSA | 424000 | [6 empty] | 424000
CSA | 456000 | 456000
CSA | 456000 | 456000
CSA | 456000 | 456000
CSA | 456000 | 456000
ESA | 456000 |  |  | 456000
ESA | 456000 |  |  | 456000
ESA | 456000 |  |  | 456000
PCA | 456000 |  |  |  | 456000
WSA | 456000 | [6 empty] | 456000
WSA | 456000 | [6 empty] | 456000
WSA | 456000 | [6 empty] | 456000
SHA | 456053.877 |  |  |  |  | 456053.877
WSA | 456053.877 | [6 empty] | 456053.877
WSA | 474494.039 | [6 empty] | 474494.039
WSA | 478002.263 | [6 empty] | 478002.263
CSA | 500000 | 500000
CSA | 500000 | 500000
CSA | 500000 | 500000
CSA | 500000 | 500000
DCA | 500000 |  | 500000
PCA | 500000 |  |  |  | 500000
SHA | 500000 |  |  |  |  | 500000
WHA | 500000 | [5 empty] | 500000
WSA | 500000 | [6 empty] | 500000
WSA | 500000 | [6 empty] | 500000
WSA | 500000 | [6 empty] | 500000
WSA | 500000 | [6 empty] | 500000
WSA | 500000 | [6 empty] | 500000
WSA | 500000 | [6 empty] | 500000
WSA | 500000 | [6 empty] | 500000
WSA | 500000 | [6 empty] | 500000
WSA | 500000 | [6 empty] | 500000
WSA | 500000 | [6 empty] | 500000
WSA | 500000 | [6 empty] | 500000
WSA | 500000 | [6 empty] | 500000
WSA | 500053.877 | [6 empty] | 500053.877
ESA | 511406.003 |  |  | 511406.003
CSA | 512528.263 | 512528.263
WSA | 515465.775 | [6 empty] | 515465.775
WSA | 515465.775 | [6 empty] | 515465.775
CSA | 524693.175 | 524693.175
CSA | 532000 | 532000
CSA | 532000 | 532000
CSA | 532000 | 532000
ESA | 532000 |  |  | 532000
ESA | 532000 |  |  | 532000
WSA | 532646.524 | [6 empty] | 532646.524
ESA | 536772.913 |  |  | 536772.913
CSA | 538970.58 | 538970.58
WSA | 544000 | [6 empty] | 544000
WSA | 561955.612 | [6 empty] | 561955.612
WHA | 565767.896 | [5 empty] | 565767.896
CSA | 566203.2977 | 566203.2977
DCA | 573323.659 |  | 573323.659
WSA | 574688.653 | [6 empty] | 574688.653
DCA | 576000 |  | 576000
SHA | 576000 |  |  |  |  | 576000
WHA | 576000 | [5 empty] | 576000
WHA | 576000 | [5 empty] | 576000
WSA | 576000 | [6 empty] | 576000
WSA | 576000 | [6 empty] | 576000
WSA | 576000 | [6 empty] | 576000
WSA | 576000 | [6 empty] | 576000
WSA | 576000 | [6 empty] | 576000
WSA | 576000 | [6 empty] | 576000
WSA | 588984.357 | [6 empty] | 588984.357
CSA | 608000 | 608000
SHA | 608000 |  |  |  |  | 608000
SHA | 608862.032 |  |  |  |  | 608862.032
WHA | 611513.5636 | [5 empty] | 611513.5636
WSA | 612631.7544 | [6 empty] | 612631.7544
WSA | 615580.0636 | [6 empty] | 615580.0636
PCA | 620000 |  |  |  | 620000
WHA | 620000 | [5 empty] | 620000
CSA | 652000 | 652000
CSA | 652000 | 652000
CSA | 652000 | 652000
ESA | 652000 |  |  | 652000
WHA | 652000 | [5 empty] | 652000
WSA | 652000 | [6 empty] | 652000
WSA | 652000 | [6 empty] | 652000
WSA | 652000 | [6 empty] | 652000
DCA | 667426.331 |  | 667426.331
CSA | 696000 | 696000
WHA | 696000 | [5 empty] | 696000
WHA | 696000 | [5 empty] | 696000
CSA | 712809.624 | 712809.624
CSA | 728000 | 728000
DCA | 728000 |  | 728000
SHA | 728000 |  |  |  |  | 728000
CSA | 751007.9106 | 751007.9106
WSA | 752371.158 | [6 empty] | 752371.158
WSA | 760000 | [6 empty] | 760000
WSA | 771018.819 | [6 empty] | 771018.819
CSA | 790877.397 | 790877.397
WSA | 803781.9591 | [6 empty] | 803781.9591
CSA | 825660.9856 | 825660.9856
ESA | 825660.9856 |  |  | 825660.9856
SHA | 825660.9856 |  |  |  |  | 825660.9856
WHA | 825660.9856 | [5 empty] | 825660.9856
WSA | 825660.9856 | [6 empty] | 825660.9856
WSA | 825660.9856 | [6 empty] | 825660.9856
CSA | 872620.872 | 872620.872
SHA | 880000 |  |  |  |  | 880000
CSA | 901660.9856 | 901660.9856
CSA | 901660.9856 | 901660.9856
CSA | 901660.9856 | 901660.9856
ESA | 901660.9856 |  |  | 901660.9856
ESA | 901660.9856 |  |  | 901660.9856
ESA | 901660.9856 |  |  | 901660.9856
ESA | 901660.9856 |  |  | 901660.9856
ESA | 901660.9856 |  |  | 901660.9856
WSA | 901660.9856 | [6 empty] | 901660.9856
WSA | 901660.9856 | [6 empty] | 901660.9856
ESA | 905432.3756 |  |  | 905432.3756
SHA | 913567.8026 |  |  |  |  | 913567.8026
WHA | 945660.9856 | [5 empty] | 945660.9856
WSA | 945660.9856 | [6 empty] | 945660.9856
CSA | 950150.792 | 950150.792
ESA | 952267.5666 |  |  | 952267.5666
WSA | 967139.556 | [6 empty] | 967139.556
CSA | 977660.9856 | 977660.9856
ESA | 977660.9856 |  |  | 977660.9856
ESA | 977660.9856 |  |  | 977660.9856
PCA | 977660.9856 |  |  |  | 977660.9856
PCA | 977660.9856 |  |  |  | 977660.9856
SHA | 977660.9856 |  |  |  |  | 977660.9856
WSA | 977660.9856 | [6 empty] | 977660.9856
WSA | 977984.2476 | [6 empty] | 977984.2476
CSA | 979762.1886 | 979762.1886
CSA | 980408.7126 | 980408.7126
CSA | 983695.2096 | 983695.2096
ESA | 985096.0116 |  |  | 985096.0116
SHA | 988598.0166 |  |  |  |  | 988598.0166
PCA | 995239.3728 |  |  |  | 995239.3728
ESA | 1008909.6456 |  |  | 1008909.6456
ESA | 1013972.554 |  |  | 1013972.554
CSA | 1017807.122 | 1017807.122
ESA | 1021660.9856 |  |  | 1021660.9856
PCA | 1021660.9856 |  |  |  | 1021660.9856
WSA | 1021660.9856 | [6 empty] | 1021660.9856
WSA | 1021660.9856 | [6 empty] | 1021660.9856
WSA | 1021660.9856 | [6 empty] | 1021660.9856
WHA | 1032544.1396 | [5 empty] | 1032544.1396
WSA | 1040661.65 | [6 empty] | 1040661.65
ESA | 1044108.8015 |  |  | 1044108.8015
CSA | 1053660.9856 | 1053660.9856
CSA | 1053660.9856 | 1053660.9856
CSA | 1053660.9856 | 1053660.9856
CSA | 1053660.9856 | 1053660.9856
ESA | 1053660.9856 |  |  | 1053660.9856
PCA | 1053660.9856 |  |  |  | 1053660.9856
SHA | 1053660.9856 |  |  |  |  | 1053660.9856
SHA | 1053660.9856 |  |  |  |  | 1053660.9856
WSA | 1053660.9856 | [6 empty] | 1053660.9856
PCA | 1053714.8626 |  |  |  | 1053714.8626
CSA | 1056853.0151 | 1056853.0151
CSA | 1058402.1616 | 1058402.1616
CSA | 1063143.3376 | 1063143.3376
WSA | 1064512.797 | [6 empty] | 1064512.797
PCA | 1065660.9856 |  |  |  | 1065660.9856
WHA | 1065660.9856 | [5 empty] | 1065660.9856
WHA | 1065660.9856 | [5 empty] | 1065660.9856
WSA | 1069015.9306 | [6 empty] | 1069015.9306
WSA | 1073473.1506 | [6 empty] | 1073473.1506
CSA | 1097660.9856 | 1097660.9856
ESA | 1097660.9856 |  |  | 1097660.9856
ESA | 1097660.9856 |  |  | 1097660.9856
SHA | 1097714.8626 |  |  |  |  | 1097714.8626
SHA | 1114690.6436 |  |  |  |  | 1114690.6436
WHA | 1120504.8336 | [5 empty] | 1120504.8336
WSA | 1125100.1946 | [6 empty] | 1125100.1946
WSA | 1129384.5174 | [6 empty] | 1129384.5174
SHA | 1129660.9856 |  |  |  |  | 1129660.9856
WSA | 1130523.0176 | [6 empty] | 1130523.0176
CSA | 1136791.5036 | 1136791.5036
WSA | 1141660.9856 | [6 empty] | 1141660.9856
WSA | 1157388.7612 | [6 empty] | 1157388.7612
WSA | 1161617.4705 | [6 empty] | 1161617.4705
PCA | 1173660.9856 |  |  |  | 1173660.9856
WHA | 1173660.9856 | [5 empty] | 1173660.9856
WSA | 1173660.9856 | [6 empty] | 1173660.9856
WSA | 1173660.9856 | [6 empty] | 1173660.9856
ESA | 1175546.6806 |  |  | 1175546.6806
WHA | 1202180.8025 | [5 empty] | 1202180.8025
ESA | 1215500.072 |  |  | 1215500.072
ESA | 1217660.9856 |  |  | 1217660.9856
WSA | 1217660.9856 | [6 empty] | 1217660.9856
WHA | 1237231.2146 | [5 empty] | 1237231.2146
ESA | 1244736.3745 |  |  | 1244736.3745
WHA | 1249660.9856 | [5 empty] | 1249660.9856
SHA | 1281660.9856 |  |  |  |  | 1281660.9856
CSA | 1293532.6796 | 1293532.6796
WHA | 1314942.4006 | [5 empty] | 1314942.4006
WHA | 1329969.2333 | [5 empty] | 1329969.2333
WHA | 1335197.2146 | [5 empty] | 1335197.2146
CSA | 1397867.4556 | 1397867.4556
WHA | 1407438.7881 | [5 empty] | 1407438.7881
SHA | 1412191.9736 |  |  |  |  | 1412191.9736
WHA | 1428394.3796 | [5 empty] | 1428394.3796
WSA | 1438358.6866 | [6 empty] | 1438358.6866
SHA | 1442518.2987 |  |  |  |  | 1442518.2987
WSA | 1469450.8811 | [6 empty] | 1469450.8811
ESA | 1512197.8858 |  |  | 1512197.8858
WSA | 1529373.8106 | [6 empty] | 1529373.8106
WHA | 1580394.3796 | [5 empty] | 1580394.3796
WSA | 1624491.6003 | [6 empty] | 1624491.6003
CSA | 1808945.6992 | 1808945.6992
WSA | 1940491.1998 | [6 empty] | 1940491.1998
WSA | 2079141.6598 | [6 empty] | 2079141.6598
CSA | 2130000 | 2130000
ESA | 2130000 |  |  | 2130000
PCA | 2130000 |  |  |  | 2130000
WSA | 2130000 | [6 empty] | 2130000
CSA | 2130053.877 | 2130053.877
WSA | 2150527.137 | [6 empty] | 2150527.137
WSA | 2156249.389 | [6 empty] | 2156249.389
WSA | 2174000 | [6 empty] | 2174000
CSA | 2206000 | 2206000
CSA | 2206000 | 2206000
ESA | 2206000 |  |  | 2206000
ESA | 2217152.539 |  |  | 2217152.539
ESA | 2250000 |  |  | 2250000
CSA | 2282000 | 2282000
ESA | 2282000 |  |  | 2282000
ESA | 2282000 |  |  | 2282000
WSA | 2326000 | [6 empty] | 2326000
CSA | 2354626.196 | 2354626.196
ESA | 2370000 |  |  | 2370000
WSA | 2447957.081 | [6 empty] | 2447957.081
CSA | 2452857.0795 | 2452857.0795
CSA | 2462400.5943 | 2462400.5943
WSA | 2488214.108 | [6 empty] | 2488214.108
ESA | 2598000 |  |  | 2598000
CSA | 2604249.732 | 2604249.732
WSA | 2647467.0068 | [6 empty] | 2647467.0068
ESA | 2651660.9856 |  |  | 2651660.9856
WSA | 2651660.9856 | [6 empty] | 2651660.9856
CSA | 2653385.0496 | 2653385.0496
WSA | 2657102.5626 | [6 empty] | 2657102.5626
WSA | 2664106.5726 | [6 empty] | 2664106.5726
CSA | 2682959.3129 | 2682959.3129
ESA | 2694229.512 |  |  | 2694229.512
ESA | 2695660.9856 |  |  | 2695660.9856
ESA | 2727660.9856 |  |  | 2727660.9856
PCA | 2727660.9856 |  |  |  | 2727660.9856
WSA | 2727660.9856 | [6 empty] | 2727660.9856
ESA | 2771660.9856 |  |  | 2771660.9856
WSA | 2816106.5726 | [6 empty] | 2816106.5726
ESA | 2849546.6806 |  |  | 2849546.6806
ESA | 2891660.9856 |  |  | 2891660.9856
CSA | 2913090.1524 | 2913090.1524
WSA | 2923660.9856 | [6 empty] | 2923660.9856
SHA | 2942697.0756 |  |  |  |  | 2942697.0756
ESA | 2999660.9856 |  |  | 2999660.9856
CSA | 3003655.3476 | 3003655.3476
CSA | 3031660.9856 | 3031660.9856
ESA | 3039419.2736 |  |  | 3039419.2736
CSA | 3060976.8373 | 3060976.8373
PCA | 3077240.7798 |  |  |  | 3077240.7798
WSA | 3124240.4256 | [6 empty] | 3124240.4256
WSA | 3129214.7712 | [6 empty] | 3129214.7712
ESA | 3565380.7122 |  |  | 3565380.7122

## Capacitors
FeederId | SectionId | Phasing | PhsCond | FeetLong | >=90% | Service Area | UPGRADE | OH or UG | UpgradeConductor | Capacitor
13021 | 13021-74750346 | ABCN | 4/0 AAAC | 155 | 119.3642 | CSA | Yes | OH | 336 ACSR | CBC0650
13029 | 13027-75701848 | ABCN | 6 CU | 182 | 91.6121 | CSA | Yes | OH | 336 ACSR | CBC0432
13065 | 13065-74307290 | ABCN | 4/0 AAAC | 123 | 143.6 | WSA | Yes | OH | 336 ACSR | CBC0919
13067 | 13067-73102508 | ABCN | 2/0 AAAC | 72 | 96.8244 | WSA | Yes | OH | 336 ACSR | CBC0999
13154 | 13154-73001492 | ABCN | 4/0 AAAC | 146 | 102.1057 | WSA | Yes | OH | 336 ACSR | CBC0769
13154 | 13154-10153285 | ABCN | 4/0 AAAC | 180 | 106.3536 | WSA | Yes | OH | 336 ACSR | CBC0767
13207 | 13207-10168552 | ABCN | 2/0 AAAC | 133 | 108.1056 | WSA | Yes | OH | 336 ACSR | CBC0883
13351 | 13348-74853526 | ABCN | 2 AAAC | 129 | 119.8602 | CSA | Yes | OH | 336 ACSR | CBC0532
13371 | 13371-75901301 | ABCN | 2 AAAC | 137 | 140.6724 | WHA | Yes | OH | 336 ACSR | CBC1135
13377 | 13359-75850486 | ABCN | 2 AAAC | 102 | 106.0753 | WSA | Yes | OH | 336 ACSR | CBC0947
13442 | 13442-10578457 | ABCN | 4/0 AAAC | 119 | 90.1178 | WHA | Yes | OH | 336 ACSR | CBC1073
13517 | 13517-10241943 | ABCN | 2/0 AAAC | 143 | 102.1571 | WSA | Yes | OH | 336 ACSR | CBC0770
13678 | 13679-73503507 | ABCN | 2/0 AAAC | 186 | 98.7552 | WSA | Yes | OH | 336 ACSR | CBC0579
13885 | 13885-76104521 | ABCN | 2/0 AAAC | 186 | 97.5596 | ESA | Yes | OH | 336 ACSR | CBC0172