## Calculations
2016 TYSP Update (ICL retired, only 60 MW ECOGEN, OCEC increase in MWs, and TP6 & 7 delayed to 2031 & 2032)
SUMMER
| -1 | -2 | -3 | -4 | -5 | -6 | -7 | -8 | -9 | -10 | -11 | -12 | -13 | -14 | -15 | -16 | -17 | -18 | -19 |  |  |  |  | BEFORE UNIT ADDITIONS
| -4: =(1)+(2)+(3); -8: =(5)+(6)-(7); -9: =(4)-(8); -10: =(9)/(8); -11: =(4)-((5)+(6)); -12: =(11)/((5)+(6)); -13: =((8)*(1+RM))-(4); -14: =(13)/(1+RM)); -15: =((5)+(6))*(1+RM_Gen_Only)-(4) | [9 empty] | Before Unit | Before Unit
| -16: Need driven by | [8 empty] | Before Unit | Additions | Additions
| -13: Generation; -14: DSM; -15: Generation; -16: Generation; -19: RM needed to | [5 empty] | Before Unit | Before Unit | Before Unit | Additions | Generation | Generation |  |  | PPA Calculation Before NPGU
| -12: Forecast; -13: Only MW; -14: Only MW; -15: Only MW; -16: Only MW; -18: New; -19: match 10% need |  |  |  | Total | Before Unit | Additions | Additions | Additions | Forecast | Only MW | Only MW
| Projections | [7 empty] | Forecast | Forecast | Forecast | of Summer | Needed to | Needed to | Needed to | Needed to | Calculated | Forecast | Forecast |  |  |  | Annual | Additions | Forecast | Forecast | Forecast | of Summer | Needed to | Needed to |  | After |  |  | After
| of Existing | New | Firm | Projection |  |  | Summer | Forecast | of | of | of Summer | Res. Margins | Meet | Meet | Meet | Meet | Capacity | Summer | of |  |  | Annual | Unit | Projection | of | of | of Summer | Res. Margins | Meet | Meet |  | Some | PPA | PPA | PPA
August | FPL Unit | Capacity | Capacity | of Total | Load | New | DSM | of Firm | Summer | Summer | Reserves | Gen Only RM | Reserve | Reserve | Gen Only RM | Gen Only RM | with MW | Reserves | Summer | August |  | New Unit | Retirements | of Total | Summer | Summer | Reserves | Gen Only RM | Reserve | Gen Only RM | August | Additions | Additions | Additions | Additions
of the | Capability | Additions | Purchases | Capacity | Forecast | Sales | Capability | Peak | Reserves | Res.Margins | without DSM | without DSM | Margin | Margin | without DSM | without DSM | addition | Calc | Res.Margins | of the |  | Additions | or Outages | Capacity | Reserves | Res.Margins | without DSM | without DSM | Margin | without DSM | of the | Need | Calc |  | Need
Year | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (MW) | (%) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | Year |  | (MW) | (MW) | (MW) | (MW) | (%) | (MW) | (%) | (MW) | (MW) | Year | (MW) | (MW) | (MW) | (MW)
2016 | 25275.5286 | 1237 | 725.5 | 27238.0286 | 24169.6865 | 0 | 1842.4667 | 22327.2199 | 4910.8088 | 21.99% | 3068.3421 | 12.7% | -445.3648 | -371.1373 | -651.3734 | 0 | 27238.0286 | 4910.8088 | 20% | 2016 | 1237 | 1237 | 0 | 26001.0286 | 3673.8088 | 16.45% | 1831.3421 | 7.577% | 791.6352 | 585.6266 | 2016 | -445.3648 | 0 | 0 | -445.3648
2017 | 23033.2329 | 3023.22 | 825.5 | 26881.9529 | 24336.0406 | 0 | 1934.8049 | 22401.2357 | 4480.7172 | 20% | 2545.9123 | 10.46% | -0.47004 | -0.3917 | -112.3082 | 0 | 26881.9529 | 4480.7172 | 20% | 2017 | 3023.22 | 1786.22 | -1469.2 | 26564.9329 | 4163.6972 | 18.59% | 2228.8923 | 9.159% | 316.55 | 204.7118 | 2017 | -0.47004 | 0 | 0 | -0.47004
2018 | 23014.1378 | 3293.8713 | 825.5 | 27133.5091 | 24606.279 | 0 | 1995.2014 | 22611.0775 | 4522.4316 | 20% | 2527.2302 | 10.27% | -0.21608 | -0.18007 | -66.6023 | 0 | 27133.5091 | 4522.4316 | 20% | 2018 | 3293.8713 | 324 | 0 | 26809.5091 | 4198.4316 | 18.57% | 2203.2302 | 8.954% | 323.7839 | 257.3977 | 2018 | -0.21608 | 0 | 0 | -0.21608
2019 | 23054.0433 | 4671.5237 | 825.5 | 28551.067 | 24893.0945 | 0 | 2041.4457 | 22851.6488 | 5699.4183 | 24.94% | 3657.9726 | 14.69% | -1129.0885 | -940.9071 | -1168.6631 | 0 | 28551.067 | 5699.4183 | 20% | 2019 | 4671.5237 | 1702 | 0 | 26849.067 | 3997.4183 | 17.49% | 1955.9726 | 7.857% | 572.9115 | 533.3369 | 2019 | -1129.0885 | 0 | 0 | -1129.0885
2020 | 23053.9494 | 4827.1772 | 113.5 | 27994.6266 | 25205.9285 | 0 | 2088.4622 | 23117.4663 | 4877.1602 | 21.1% | 2788.698 | 11.06% | -253.667 | -211.3891 | -268.1052 | 0 | 27994.6266 | 4877.1602 | 20% | 2020 | 4827.1772 | 156 | 0 | 27838.6266 | 4721.1602 | 20.42% | 2632.698 | 10.44% | -97.667 | -112.1052 | 2020 | -253.667 | 0 | 0 | -253.667
2021 | 23141.8561 | 5035.6168 | 173.5 | 28350.9729 | 25316.4163 | 0 | 2136.2343 | 23180.1819 | 5170.791 | 22.31% | 3034.5567 | 11.99% | -534.7546 | -445.6289 | -502.9151 | -502.9151 | 27848.0579 | 4667.876 | 20% | 2021 | 5035.6168 | 209.2532 | 0 | 28141.7198 | 4961.5379 | 21.4% | 2825.3035 | 11.16% | -325.5015 | -293.6619 | 2021 | -502.9151 | 0 | 0 | -502.9151
2022 | 23227.7635 | 5287.9878 | 173.5 | 28689.2513 | 25540.1892 | 0 | 2184.7465 | 23355.4427 | 5333.8086 | 22.84% | 3149.0621 | 12.33% | -662.72 | -552.2667 | -595.0431 | -595.0431 | 28094.2081 | 4738.7654 | 20% | 2022 | 5287.9878 | 253.8098 | 0 | 28435.4414 | 5079.9987 | 21.75% | 2895.2522 | 11.34% | -408.9102 | -341.2333 | 2022 | -595.0431 | 0 | 0 | -595.0431
2023 | 23227.6714 | 5494.7367 | 173.5 | 28895.9081 | 25832.9033 | 0 | 2234.0295 | 23598.8738 | 5297.0343 | 22.45% | 3063.0048 | 11.86% | -577.2596 | -481.0496 | -479.7145 | -479.7145 | 28416.1936 | 4817.3198 | 20% | 2023 | 5494.7367 | 208.8098 | 0 | 28687.0982 | 5088.2245 | 21.56% | 2854.195 | 11.05% | -368.4497 | -270.9047 | 2023 | -479.7145 | 0 | 0 | -479.7145
2024 | 23229.5799 | 5492.0555 | 173.5 | 28895.1354 | 26180.2785 | 0 | 2284.1822 | 23896.0963 | 4999.0391 | 20.92% | 2714.8569 | 10.37% | -219.8198 | -183.1832 | -96.829 | -96.829 | 28798.3064 | 4902.2101 | 20% | 2024 | 5492.0555 | 0 | 0 | 28895.1354 | 4999.0391 | 20.92% | 2714.8569 | 10.37% | -219.8198 | -96.829 | 2024 | -96.829 | 0 | 0 | -96.829
2025 | 23229.4891 | 5826.7323 | 173.5 | 29229.7214 | 26572.456 | 0 | 2334 | 24238.456 | 4991.2654 | 20.59% | 2657.2654 | 10% | -143.5741 | -119.6451 | -0.01975 | -0.01975 | 29229.7016 | 4991.2456 | 20% | 2025 | 5826.7323 | 337.35 | 0 | 28892.3714 | 4653.9154 | 19.2% | 2319.9154 | 8.731% | 193.7759 | 337.3303 | 2025 | -0.01975 | 0 | 0 | -0.01975
2026 | 23229.3988 | 6372.0671 | 173.5 | 29774.9659 | 27067.6001 | 0 | 2384 | 24683.6001 | 5091.3659 | 20.63% | 2707.3659 | 10% | -154.6458 | -128.8715 | -0.60585 | -0.60585 | 29774.3601 | 5090.76 | 20% | 2026 | 6372.0671 | 630 | 0 | 29144.9659 | 4461.3659 | 18.07% | 2077.3659 | 7.675% | 475.3542 | 629.3941 | 2026 | -0.60585 | 0 | 0 | -0.60585
2027 | 23229.3091 | 8040.41 | 170 | 31439.7191 | 27665.2192 | 0 | 2434 | 25231.2192 | 6208.4999 | 24.61% | 3774.4999 | 13.64% | -1162.2561 | -968.5468 | -1007.978 | -1007.978 | 30431.7411 | 5200.5219 | 20% | 2027 | 8040.41 | 1751 | 0 | 29688.7191 | 4457.4999 | 17.67% | 2023.4999 | 7.314% | 588.7439 | 743.022 | 2027 | -1007.978 | 0 | 0 | -1007.978
2028 | 23229.22 | 8037.7608 | 170 | 31436.9808 | 28224.7243 | 0 | 2484 | 25740.7243 | 5696.2565 | 22.13% | 3212.2565 | 11.38% | -548.1116 | -456.7597 | -389.7841 | -389.7841 | 31047.1967 | 5306.4724 | 20% | 2028 | 8037.7608 | 0 | 0 | 31436.9808 | 5696.2565 | 22.13% | 3212.2565 | 11.38% | -548.1116 | -389.7841 | 2028 | -389.7841 | 0 | 0 | -389.7841
2029 | 23229.1315 | 8287.1196 | 170 | 31686.2511 | 28804.8144 | 0 | 2534 | 26270.8144 | 5415.4367 | 20.61% | 2881.4367 | 10% | -161.2738 | -134.3948 | -0.95525 | -0.95525 | 31685.2958 | 5414.4814 | 20% | 2029 | 8287.1196 | 252 | 0 | 31434.2511 | 5163.4367 | 19.65% | 2629.4367 | 9.128% | 90.7262 | 251.0448 | 2029 | -0.95525 | 0 | 0 | -0.95525
2030 | 23229.0435 | 8897.1863 | 170 | 32296.2298 | 29397.6618 | 0 | 2584 | 26813.6618 | 5482.568 | 20.45% | 2898.568 | 9.86% | -119.8356 | -99.863 | 41.1982 | 41.1982 | 32337.428 | 5523.7662 | 20.6% | 2030 | 8897.1863 | 664.7 | 0 | 31631.5298 | 4817.868 | 17.97% | 2233.868 | 7.599% | 544.8644 | 705.8982 | 2030 | 41.1982 | 41.1982 | 0 | 41.1982
2031 | 23228.9561 | 9509.1785 | 170 | 32908.1346 | 29916.486 | 0 | 2584 | 27332.486 | 5575.6486 | 20.4% | 2991.6486 | 10% | -109.1514 | -90.9595 | 0 | 0 | 32908.1346 | 5575.6486 | 20% | 2031 | 9509.1785 | 614.6176 | 0 | 32293.517 | 4961.031 | 18.15% | 2377.031 | 7.946% | 505.4662 | 614.6176 | 2031 | 0 | 0 | 0 | 0
2032 | 22397.8693 | 11257.5609 | 170 | 33825.4302 | 30478.7122 | 0 | 2584 | 27894.7122 | 5930.718 | 21.26% | 3346.718 | 10.98% | -351.7756 | -293.1463 | -298.8468 | -298.8468 | 33526.5834 | 5631.8712 | 20% | 2032 | 11257.5609 | 1751 | -831 | 32905.4302 | 5010.718 | 17.96% | 2426.718 | 7.962% | 568.2244 | 621.1532 | 2032 | -298.8468 | 0 | 0 | -298.8468
2033 | 21556.7831 | 13005.9513 | 170 | 34732.7343 | 31014.602 | 0 | 2584 | 28430.602 | 6302.1323 | 22.17% | 3718.1323 | 11.99% | -616.0119 | -513.3432 | -616.6721 | 0 | 34732.7343 | 6302.1323 | 20% | 2033 | 13005.9513 | 1751 | -841 | 33822.7343 | 5392.1323 | 18.97% | 2808.1323 | 9.054% | 293.9881 | 293.3279 | 2033 | -616.0119 | 0 | 0 | -616.0119
2034 | 21556.6974 | 13878.8494 | 60 | 35495.5468 | 31496.9298 | 0 | 2584 | 28912.9298 | 6582.617 | 22.77% | 3998.617 | 12.7% | -800.031 | -666.6925 | -848.924 | 0 | 35495.5468 | 6582.617 | 20% | 2034 | 13878.8494 | 875.5 | 0 | 34620.0468 | 5707.117 | 19.74% | 3123.117 | 9.916% | 75.469 | 26.576 | 2034 | -800.031 | 0 | 0 | -800.031
2035 | 21556.6122 | 13876.2554 | 60 | 35492.8676 | 31985.1039 | 0 | 2584 | 29401.1039 | 6091.7637 | 20.72% | 3507.7637 | 10.97% | -211.5429 | -176.2857 | -309.2533 | 0 | 35492.8676 | 6091.7637 | 20% | 2035 | 13876.2554 | 0 | 0 | 35492.8676 | 6091.7637 | 20.72% | 3507.7637 | 10.97% | -211.5429 | -309.2533 | 2035 | -211.5429 | 0 | 0 | -211.5429
2036 | 20575.5277 | 15624.6691 | 60 | 36260.1968 | 32468.0191 | 0 | 2584 | 29884.0191 | 6376.1777 | 21.34% | 3792.1777 | 11.68% | -399.3738 | -332.8115 | -545.3758 | 0 | 36260.1968 | 6376.1777 | 20% | 2036 | 15624.6691 | 1751 | -981 | 35490.1968 | 5606.1777 | 18.76% | 3022.1777 | 9.308% | 370.6262 | 224.6242 | 2036 | -399.3738 | 0 | 0 | -399.3738
2037 | 20575.4436 | 16497.5906 | 60 | 37133.0342 | 32926.0632 | 0 | 2584 | 30342.0632 | 6790.971 | 22.38% | 4206.971 | 12.78% | -722.5584 | -602.132 | -914.3647 | 0 | 37133.0342 | 6790.971 | 20% | 2037 | 16497.5906 | 875.5 | 0 | 36257.5342 | 5915.471 | 19.5% | 3331.471 | 10.12% | 152.9416 | -38.8647 | 2037 | -722.5584 | 0 | 0 | -722.5584
2038 | 20575.3601 | 16495.0198 | 60 | 37130.38 | 33401.2155 | 0 | 2584 | 30817.2155 | 6313.1644 | 20.49% | 3729.1644 | 11.16% | -149.7213 | -124.7678 | -389.0429 | 0 | 37130.38 | 6313.1644 | 20% | 2038 | 16495.0198 | 0 | 0 | 37130.38 | 6313.1644 | 20.49% | 3729.1644 | 11.16% | -149.7213 | -389.0429 | 2038 | -149.7213 | 0 | 0 | -149.7213
2039 | 20575.2772 | 17367.9568 | 60 | 38003.234 | 33877.6204 | 0 | 2584 | 31293.6204 | 6709.6136 | 21.44% | 4125.6136 | 12.18% | -450.8895 | -375.7413 | -737.8516 | 0 | 38003.234 | 6709.6136 | 20% | 2039 | 17367.9568 | 875.5 | 0 | 37127.734 | 5834.1136 | 18.64% | 3250.1136 | 9.594% | 424.6105 | 137.6484 | 2039 | -450.8895 | 0 | 0 | -450.8895
2040 | 20575.1948 | 18240.9014 | 60 | 38876.0962 | 34362.1064 | 0 | 2584 | 31778.1064 | 7097.9898 | 22.34% | 4513.9898 | 13.14% | -742.3686 | -618.6405 | -1077.7792 | 0 | 38876.0962 | 7097.9898 | 20% | 2040 | 18240.9014 | 875.5 | 0 | 38000.5962 | 6222.4898 | 19.58% | 3638.4898 | 10.59% | 133.1314 | -202.2792 | 2040 | -742.3686 | 0 | 0 | -742.3686
2041 | 20575.1129 | 18238.3537 | 60 | 38873.4666 | 34752.544 | 0 | 2584 | 32168.544 | 6704.9226 | 20.84% | 4120.9226 | 11.86% | -271.2138 | -226.0115 | -645.6682 | 0 | 38873.4666 | 6704.9226 | 20% | 2041 | 18238.3537 | 0 | 0 | 38873.4666 | 6704.9226 | 20.84% | 4120.9226 | 11.86% | -271.2138 | -645.6682 | 2041 | -271.2138 | 0 | 0 | -271.2138
2042 | 20575.0316 | 19111.3136 | 60 | 39746.3452 | 35143.6793 | 0 | 2584 | 32559.6793 | 7186.666 | 22.07% | 4602.666 | 13.1% | -674.7301 | -562.2751 | -1088.2981 | 0 | 39746.3452 | 7186.666 | 20% | 2042 | 19111.3136 | 875.5 | 0 | 38870.8452 | 6311.166 | 19.38% | 3727.166 | 10.61% | 200.7699 | -212.7981 | 2042 | -674.7301 | 0 | 0 | -674.7301
2043 | 19734.9508 | 19984.2812 | 60 | 39779.232 | 35535.5131 | 0 | 2584 | 32951.5131 | 6827.7189 | 20.72% | 4243.7189 | 11.94% | -237.4163 | -197.8469 | -690.1676 | 0 | 39779.232 | 6827.7189 | 20% | 2043 | 19984.2812 | 875.5 | -840 | 39743.732 | 6792.2189 | 20.61% | 4208.2189 | 11.84% | -201.9163 | -654.6676 | 2043 | -237.4163 | 0 | 0 | -237.4163
2044 | 19734.8705 | 20857.2564 | 60 | 40652.1269 | 35928.0467 | 0 | 2584 | 33344.0467 | 7308.0802 | 21.92% | 4724.0802 | 13.15% | -639.2709 | -532.7257 | -1131.2755 | 0 | 40652.1269 | 7308.0802 | 20% | 2044 | 20857.2564 | 875.5 | 0 | 39776.6269 | 6432.5802 | 19.29% | 3848.5802 | 10.71% | 236.2291 | -255.7755 | 2044 | -639.2709 | 0 | 0 | -639.2709
2045 | 19734.7908 | 20854.7391 | 60 | 40649.5299 | 36321.2811 | 0 | 2584 | 33737.2811 | 6912.2488 | 20.49% | 4328.2488 | 11.92% | -164.7926 | -137.3272 | -696.1207 | 0 | 40649.5299 | 6912.2488 | 20% | 2045 | 20854.7391 | 0 | 0 | 40649.5299 | 6912.2488 | 20.49% | 4328.2488 | 11.92% | -164.7926 | -696.1207 | 2045 | -164.7926 | 0 | 0 | -164.7926
2046 | 19734.7115 | 21727.7294 | 60 | 41522.4409 | 36715.2173 | 0 | 2584 | 34131.2173 | 7391.2236 | 21.66% | 4807.2236 | 13.09% | -564.9801 | -470.8168 | -1135.7019 | 0 | 41522.4409 | 7391.2236 | 20% | 2046 | 21727.7294 | 875.5 | 0 | 40646.9409 | 6515.7236 | 19.09% | 3931.7236 | 10.71% | 310.5199 | -260.2019 | 2046 | -564.9801 | 0 | 0 | -564.9801
2047 | 19734.6328 | 21725.2272 | 60 | 41519.86 | 37109.8565 | 0 | 2584 | 34525.8565 | 6994.0035 | 20.26% | 4410.0035 | 11.88% | -88.8322 | -74.0268 | -699.0178 | 0 | 41519.86 | 6994.0035 | 20% | 2047 | 21725.2272 | 0 | 0 | 41519.86 | 6994.0035 | 20.26% | 4410.0035 | 11.88% | -88.8322 | -699.0178 | 2047 | -88.8322 | 0 | 0 | -88.8322
2048 | 19734.5546 | 22598.2325 | 60 | 42392.7871 | 37505.1998 | 0 | 2584 | 34921.1998 | 7471.5873 | 21.4% | 4887.5873 | 13.03% | -487.3473 | -406.1228 | -1137.0673 | 0 | 42392.7871 | 7471.5873 | 20% | 2048 | 22598.2325 | 875.5 | 0 | 41517.2871 | 6596.0873 | 18.89% | 4012.0873 | 10.7% | 388.1527 | -261.5673 | 2048 | -487.3473 | 0 | 0 | -487.3473
2049 | 19734.4769 | 22595.7453 | 60 | 42390.2222 | 37901.2482 | 0 | 2584 | 35317.2482 | 7072.974 | 20.03% | 4488.974 | 11.84% | -9.5244 | -7.937 | -698.8492 | 0 | 42390.2222 | 7072.974 | 20% | 2049 | 22595.7453 | 0 | 0 | 42390.2222 | 7072.974 | 20.03% | 4488.974 | 11.84% | -9.5244 | -698.8492 | 2049 | -9.5244 | 0 | 0 | -9.5244
2050 | 19734.3997 | 23468.7656 | 0 | 43203.1653 | 38298.0028 | 0 | 2584 | 35714.0028 | 7489.1624 | 20.97% | 4905.1624 | 12.81% | -346.3619 | -288.6349 | -1075.3621 | 0 | 43203.1653 | 7489.1624 | 20% | 2050 | 23468.7656 | 875.5 | 0 | 42327.6653 | 6613.6624 | 18.52% | 4029.6624 | 10.52% | 529.1381 | -199.8621 | 2050 | -346.3619 | 0 | 0 | -346.3619
2051 | 19734.323 | 24341.7933 | 0 | 44076.1163 | 38695.4648 | 0 | 2584 | 36111.4648 | 7964.6515 | 22.06% | 5380.6515 | 13.91% | -742.3585 | -618.6321 | -1511.105 | 0 | 44076.1163 | 7964.6515 | 20% | 2051 | 24341.7933 | 875.5 | 0 | 43200.6163 | 7089.1515 | 19.63% | 4505.1515 | 11.64% | 133.1415 | -635.605 | 2051 | -742.3585 | 0 | 0 | -742.3585
2052 | 19734.2468 | 24339.3284 | 0 | 44073.5752 | 39093.6352 | 0 | 2584 | 36509.6352 | 7563.94 | 20.72% | 4979.94 | 12.74% | -262.013 | -218.3441 | -1070.5765 | 0 | 44073.5752 | 7563.94 | 20% | 2052 | 24339.3284 | 0 | 0 | 44073.5752 | 7563.94 | 20.72% | 4979.94 | 12.74% | -262.013 | -1070.5765 | 2052 | -262.013 | 0 | 0 | -262.013
2053 | 19734.1711 | 25212.3709 | 0 | 44946.542 | 39487.0507 | 0 | 2584 | 36903.0507 | 8043.4913 | 21.8% | 5459.4913 | 13.83% | -662.8811 | -552.4009 | -1510.7862 | 0 | 44946.542 | 8043.4913 | 20% | 2053 | 25212.3709 | 875.5 | 0 | 44071.042 | 7167.9913 | 19.42% | 4583.9913 | 11.61% | 212.6189 | -635.2862 | 2053 | -662.8811 | 0 | 0 | -662.8811
2054 | 19734.0959 | 25209.9208 | 0 | 44944.0167 | 39881.1457 | 0 | 2584 | 37297.1457 | 7646.871 | 20.5% | 5062.871 | 12.69% | -187.4419 | -156.2016 | -1074.7564 | 0 | 44944.0167 | 7646.871 | 20% | 2054 | 25209.9208 | 0 | 0 | 44944.0167 | 7646.871 | 20.5% | 5062.871 | 12.69% | -187.4419 | -1074.7564 | 2054 | -187.4419 | 0 | 0 | -187.4419
2055 | 19734.0211 | 26082.9781 | 0 | 45816.9992 | 40275.9209 | 0 | 2584 | 37691.9209 | 8125.0783 | 21.56% | 5541.0783 | 13.76% | -586.6941 | -488.9117 | -1513.4862 | 0 | 45816.9992 | 8125.0783 | 20% | 2055 | 26082.9781 | 875.5 | 0 | 44941.4992 | 7249.5783 | 19.23% | 4665.5783 | 11.58% | 288.8059 | -637.9862 | 2055 | -586.6941 | 0 | 0 | -586.6941
2056 | 19733.9469 | 26080.5426 | 0 | 45814.4895 | 40671.3775 | 0 | 2584 | 38087.3775 | 7727.1121 | 20.29% | 5143.1121 | 12.65% | -109.6366 | -91.3638 | -1075.9743 | 0 | 45814.4895 | 7727.1121 | 20% | 2056 | 26080.5426 | 0 | 0 | 45814.4895 | 7727.1121 | 20.29% | 5143.1121 | 12.65% | -109.6366 | -1075.9743 | 2056 | -109.6366 | 0 | 0 | -109.6366
2057 | 19733.8732 | 26953.6145 | 0 | 46687.4877 | 41067.5161 | 0 | 2584 | 38483.5161 | 8203.9715 | 21.32% | 5619.9715 | 13.68% | -507.2683 | -422.7236 | -1513.2199 | 0 | 46687.4877 | 8203.9715 | 20% | 2057 | 26953.6145 | 875.5 | 0 | 45811.9877 | 7328.4715 | 19.04% | 4744.4715 | 11.55% | 368.2317 | -637.7199 | 2057 | -507.2683 | 0 | 0 | -507.2683
2058 | 19733.7999 | 26951.1937 | 0 | 46684.9935 | 41464.3379 | 0 | 2584 | 38880.3379 | 7804.6556 | 20.07% | 5220.6556 | 12.59% | -28.588 | -23.8234 | -1074.2218 | 0 | 46684.9935 | 7804.6556 | 20% | 2058 | 26951.1937 | 0 | 0 | 46684.9935 | 7804.6556 | 20.07% | 5220.6556 | 12.59% | -28.588 | -1074.2218 | 2058 | -28.588 | 0 | 0 | -28.588
2059 | 19733.7271 | 27824.2801 | 0 | 47558.0072 | 41861.8437 | 0 | 2584 | 39277.8437 | 8280.1634 | 21.08% | 5696.1634 | 13.61% | -424.5947 | -353.8289 | -1509.979 | 0 | 47558.0072 | 8280.1634 | 20% | 2059 | 27824.2801 | 875.5 | 0 | 46682.5072 | 7404.6634 | 18.85% | 4820.6634 | 11.52% | 450.9053 | -634.479 | 2059 | -424.5947 | 0 | 0 | -424.5947
2060 | 19733.6547 | 28697.3737 | 0 | 48431.0285 | 42260.0345 | 0 | 2584 | 39676.0345 | 8754.994 | 22.07% | 6170.994 | 14.6% | -819.7871 | -683.1559 | -1944.9905 | 0 | 48431.0285 | 8754.994 | 20% | 2060 | 28697.3737 | 875.5 | 0 | 47555.5285 | 7879.494 | 19.86% | 5295.494 | 12.53% | 55.7129 | -1069.4905 | 2060 | -819.7871 | 0 | 0 | -819.7871
2061 | 19733.5829 | 28694.9746 | 0 | 48428.5575 | 42658.9112 | 0 | 2584 | 40074.9112 | 8353.6464 | 20.85% | 5769.6464 | 13.53% | -338.6641 | -282.2201 | -1503.7552 | 0 | 48428.5575 | 8353.6464 | 20% | 2061 | 28694.9746 | 0 | 0 | 48428.5575 | 8353.6464 | 20.85% | 5769.6464 | 13.53% | -338.6641 | -1503.7552 | 2061 | -338.6641 | 0 | 0 | -338.6641
2062 | 19733.5115 | 29568.0827 | 0 | 49301.5942 | 43058.4746 | 0 | 2584 | 40474.4746 | 8827.1196 | 21.81% | 6243.1196 | 14.5% | -732.2246 | -610.1872 | -1937.2721 | 0 | 49301.5942 | 8827.1196 | 20% | 2062 | 29568.0827 | 875.5 | 0 | 48426.0942 | 7951.6196 | 19.65% | 5367.6196 | 12.47% | 143.2754 | -1061.7721 | 2062 | -732.2246 | 0 | 0 | -732.2246
2063 | 19733.4406 | 29565.698 | 0 | 49299.1385 | 43458.7259 | 0 | 2584 | 40874.7259 | 8424.4127 | 20.61% | 5840.4127 | 13.44% | -249.4675 | -207.8896 | -1494.5401 | 0 | 49299.1385 | 8424.4127 | 20% | 2063 | 29565.698 | 0 | 0 | 49299.1385 | 8424.4127 | 20.61% | 5840.4127 | 13.44% | -249.4675 | -1494.5401 | 2063 | -249.4675 | 0 | 0 | -249.4675
2064 | 19733.3701 | 30438.8204 | 0 | 50172.1905 | 43862.6977 | 0 | 2584 | 41278.6977 | 8893.4928 | 21.54% | 6309.4928 | 14.38% | -637.7533 | -531.4611 | -1923.2231 | 0 | 50172.1905 | 8893.4928 | 20% | 2064 | 30438.8204 | 875.5 | 0 | 49296.6905 | 8017.9928 | 19.42% | 5433.9928 | 12.39% | 237.7467 | -1047.7231 | 2064 | -637.7533 | 0 | 0 | -637.7533
2065 | 19733.3001 | 30436.4499 | 0 | 50169.75 | 44270.4246 | 0 | 2634 | 41636.4246 | 8533.3255 | 20.49% | 5899.3255 | 13.33% | -206.0406 | -171.7005 | -1472.283 | 0 | 50169.75 | 8533.3255 | 20% | 2065 | 30436.4499 | 0 | 0 | 50169.75 | 8533.3255 | 20.49% | 5899.3255 | 13.33% | -206.0406 | -1472.283 | 2065 | -206.0406 | 0 | 0 | -206.0406

## PV Calculations
2016 TYSP Update (ICL retired, only 60 MW ECOGEN, OCEC increase in MWs, and TP6 & 7 delayed to 2031 & 2032)
SUMMER
|  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072
| New Solar Unit | 0 | 223.5 | 0 | 0 | 300 | 472 | 471 | 471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Firm Capacity Value | 0% | 52% | 0% | 0% | 52% | 44.33% | 44.33% | 44.33% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Year | Total Firm Solar Capacity Added with Degradation
2016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017 | 116.22 | 0 | 116.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018 | 115.8713 | 0 | 115.8713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019 | 115.5237 | 0 | 115.5237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020 | 271.1772 | 0 | 115.1772 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 479.6168 | 0 | 114.8316 | 0 | 0 | 155.532 | 209.2532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 686.9878 | 0 | 114.4871 | 0 | 0 | 155.0654 | 208.6254 | 208.8098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023 | 893.7367 | 0 | 114.1437 | 0 | 0 | 154.6002 | 207.9995 | 208.1834 | 208.8098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024 | 891.0555 | 0 | 113.8012 | 0 | 0 | 154.1364 | 207.3755 | 207.5589 | 208.1834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025 | 888.3823 | 0 | 113.4598 | 0 | 0 | 153.674 | 206.7534 | 206.9362 | 207.5589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026 | 885.7171 | 0 | 113.1195 | 0 | 0 | 153.213 | 206.1332 | 206.3154 | 206.9362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027 | 883.06 | 0 | 112.7801 | 0 | 0 | 152.7533 | 205.5148 | 205.6964 | 206.3154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2028 | 880.4108 | 0 | 112.4418 | 0 | 0 | 152.2951 | 204.8982 | 205.0793 | 205.6964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2029 | 877.7696 | 0 | 112.1044 | 0 | 0 | 151.8382 | 204.2835 | 204.4641 | 205.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2030 | 875.1363 | 0 | 111.7681 | 0 | 0 | 151.3827 | 203.6707 | 203.8507 | 204.4641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031 | 872.5109 | 0 | 111.4328 | 0 | 0 | 150.9285 | 203.0597 | 203.2392 | 203.8507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2032 | 869.8933 | 0 | 111.0985 | 0 | 0 | 150.4757 | 202.4505 | 202.6294 | 203.2392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2033 | 867.2837 | 0 | 110.7652 | 0 | 0 | 150.0243 | 201.8431 | 202.0216 | 202.6294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2034 | 864.6818 | 0 | 110.4329 | 0 | 0 | 149.5742 | 201.2376 | 201.4155 | 202.0216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2035 | 862.0878 | 0 | 110.1016 | 0 | 0 | 149.1255 | 200.6339 | 200.8112 | 201.4155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2036 | 859.5015 | 0 | 109.7713 | 0 | 0 | 148.6781 | 200.032 | 200.2088 | 200.8112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2037 | 856.923 | 0 | 109.442 | 0 | 0 | 148.2321 | 199.4319 | 199.6082 | 200.2088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2038 | 854.3522 | 0 | 109.1137 | 0 | 0 | 147.7874 | 198.8336 | 199.0094 | 199.6082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2039 | 851.7892 | 0 | 108.7863 | 0 | 0 | 147.3441 | 198.2371 | 198.4123 | 199.0094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2040 | 849.2338 | 0 | 108.46 | 0 | 0 | 146.902 | 197.6424 | 197.8171 | 198.4123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2041 | 846.6861 | 0 | 108.1346 | 0 | 0 | 146.4613 | 197.0494 | 197.2236 | 197.8171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2042 | 844.146 | 0 | 107.8102 | 0 | 0 | 146.0219 | 196.4583 | 196.632 | 197.2236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2043 | 841.6136 | 0 | 107.4868 | 0 | 0 | 145.5839 | 195.8689 | 196.0421 | 196.632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2044 | 839.0888 | 0 | 107.1643 | 0 | 0 | 145.1471 | 195.2813 | 195.4539 | 196.0421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2045 | 836.5715 | 0 | 106.8428 | 0 | 0 | 144.7117 | 194.6955 | 194.8676 | 195.4539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2046 | 834.0618 | 0 | 106.5223 | 0 | 0 | 144.2775 | 194.1114 | 194.283 | 194.8676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2047 | 831.5596 | 0 | 106.2027 | 0 | 0 | 143.8447 | 193.5291 | 193.7001 | 194.283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2048 | 829.0649 | 0 | 105.8841 | 0 | 0 | 143.4132 | 192.9485 | 193.119 | 193.7001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2049 | 826.5777 | 0 | 105.5665 | 0 | 0 | 142.9829 | 192.3696 | 192.5397 | 193.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2050 | 824.098 | 0 | 105.2498 | 0 | 0 | 142.554 | 191.7925 | 191.9621 | 192.5397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2051 | 821.6257 | 0 | 104.934 | 0 | 0 | 142.1263 | 191.2171 | 191.3862 | 191.9621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2052 | 819.1608 | 0 | 104.6192 | 0 | 0 | 141.6999 | 190.6435 | 190.812 | 191.3862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2053 | 816.7033 | 0 | 104.3053 | 0 | 0 | 141.2748 | 190.0716 | 190.2396 | 190.812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2054 | 814.2532 | 0 | 103.9924 | 0 | 0 | 140.851 | 189.5013 | 189.6689 | 190.2396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2055 | 811.8105 | 0 | 103.6805 | 0 | 0 | 140.4285 | 188.9328 | 189.0999 | 189.6689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2056 | 809.375 | 0 | 103.3694 | 0 | 0 | 140.0072 | 188.366 | 188.5326 | 189.0999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2057 | 806.9469 | 0 | 103.0593 | 0 | 0 | 139.5872 | 187.8009 | 187.967 | 188.5326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2058 | 804.5261 | 0 | 102.7501 | 0 | 0 | 139.1684 | 187.2375 | 187.4031 | 187.967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2059 | 802.1125 | 0 | 102.4419 | 0 | 0 | 138.7509 | 186.6758 | 186.8408 | 187.4031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2060 | 799.7061 | 0 | 102.1345 | 0 | 0 | 138.3346 | 186.1158 | 186.2803 | 186.8408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2061 | 797.307 | 0 | 101.8281 | 0 | 0 | 137.9196 | 185.5574 | 185.7215 | 186.2803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2062 | 794.9151 | 0 | 101.5227 | 0 | 0 | 137.5059 | 185.0008 | 185.1643 | 185.7215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2063 | 792.5304 | 0 | 101.2181 | 0 | 0 | 137.0934 | 184.4458 | 184.6088 | 185.1643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2064 | 790.1528 | 0 | 100.9144 | 0 | 0 | 136.6821 | 183.8924 | 184.055 | 184.6088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2065 | 787.7823 | 0 | 100.6117 | 0 | 0 | 136.272 | 183.3408 | 183.5028 | 184.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## New Unit Calculations
2016 TYSP Update (ICL retired, only 60 MW ECOGEN, OCEC increase in MWs, and TP6 & 7 delayed to 2031 & 2032)
SUMMER
|  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072
| New Unit Name | 2016: PEEC; 2017: FM 2CT; PFL 5CT; 2019: OCEC; 2022: OCEC Inc MW; 2025: Battery; 2026: Battery; 2027: CC; 2029: Battery; 2030: Battery
| New Unit MW | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Year | Total New Unit Capacity Addition
2016 | 1237 | 1237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017 | 2854 | 1237 | 1617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018 | 2854 | 1237 | 1617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019 | 4556 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020 | 4556 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 4556 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 4601 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023 | 4601 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024 | 4601 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025 | 4856.35 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026 | 5406.35 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027 | 7157.35 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2028 | 7157.35 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2029 | 7357.35 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2030 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2032 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2033 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2034 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2035 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2036 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2037 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2038 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2039 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2040 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2041 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2042 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2043 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2044 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2045 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2046 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2047 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2048 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2049 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2050 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2051 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2052 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2053 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2054 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2055 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2056 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2057 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2058 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2059 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2060 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2061 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2062 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2063 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2064 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2065 | 8022.05 | 1237 | 1617 | 0 | 1702 | 0 | 0 | 45 | 0 | 0 | 255.35 | 550 | 1751 | 0 | 200 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Equalizing & Small Filler Calc
2016 TYSP Update (ICL retired, only 60 MW ECOGEN, OCEC increase in MWs, and TP6 & 7 delayed to 2031 & 2032)
SUMMER
| Eq Filler Size | 0 | [5 empty] | Was there a need in eq. filler input year? | 34
Annual # of Small Fillers Added | Cumulative Number of Small Fillers Added | Year | Total New Unit MW | Need (MW) After Large Filler Addition(s) | Size of Excess Need in Equalizaing Filler Year, if any | Checking for Equilizing Filler (MW) |  | Equalizing Filler (MW) | Need (MW) After Large Filler Addition(s) + Eq. Filler | Small Filler(s) Addition (MW) | Need (MW) After Large Filler Addition(s) + Eq. Filler + Small Filler(s) | 2031
0 | 0 | 2016 |  | -445.3648 | 0 | 0 |  | 0 | -445.3648 | 0 | -445.3648 | 0
0 | 0 | 2017 |  | -0.47004 | 0 | 0 |  | 0 | -0.47004 | 0 | -0.47004 | 0
0 | 0 | 2018 |  | -0.21608 | 0 | 0 |  | 0 | -0.21608 | 0 | -0.21608 | 0
0 | 0 | 2019 |  | -1129.0885 | 0 | 0 |  | 0 | -1129.0885 | 0 | -1129.0885 | 0
0 | 0 | 2020 |  | -253.667 | 0 | 0 |  | 0 | -253.667 | 0 | -253.667 | 0
0 | 0 | 2021 |  | -502.9151 | 0 | 0 |  | 0 | -502.9151 | 0 | -502.9151 | 0
0 | 0 | 2022 |  | -595.0431 | 0 | 0 |  | 0 | -595.0431 | 0 | -595.0431 | 0
0 | 0 | 2023 |  | -479.7145 | 0 | 0 |  | 0 | -479.7145 | 0 | -479.7145 | 0
0 | 0 | 2024 |  | -96.829 | 0 | 0 |  | 0 | -96.829 | 0 | -96.829 | 0
0 | 0 | 2025 |  | -0.01975 | 0 | 0 |  | 0 | -0.01975 | 0 | -0.01975 | 0
0 | 0 | 2026 |  | -0.60585 | 0 | 0 |  | 0 | -0.60585 | 0 | -0.60585 | 0
0 | 0 | 2027 |  | -1007.978 | 0 | 0 |  | 0 | -1007.978 | 0 | -1007.978 | 0
0 | 0 | 2028 |  | -389.7841 | 0 | 0 |  | 0 | -389.7841 | 0 | -389.7841 | 0
0 | 0 | 2029 |  | -0.95525 | 0 | 0 |  | 0 | -0.95525 | 0 | -0.95525 | 0
0 | 0 | 2030 |  | 41.1982 | 0 | 0 |  | 0 | 41.1982 | 0 | 41.1982 | 0
0 | 0 | 2031 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2031
0 | 0 | 2032 |  | -298.8468 | 0 | 0 | + | 0 | -298.8468 | 0 | -298.8468 | 0
0 | 0 | 2033 |  | -616.0119 | 0 | 0 | + | 0 | -616.0119 | 0 | -616.0119 | 0
0 | 0 | 2034 |  | -800.031 | 0 | 0 | + | 0 | -800.031 | 0 | -800.031 | 0
0 | 0 | 2035 |  | -211.5429 | 0 | 0 | + | 0 | -211.5429 | 0 | -211.5429 | 0
0 | 0 | 2036 |  | -399.3738 | 0 | 0 | + | 0 | -399.3738 | 0 | -399.3738 | 0
0 | 0 | 2037 |  | -722.5584 | 0 | 0 | + | 0 | -722.5584 | 0 | -722.5584 | 0
0 | 0 | 2038 |  | -149.7213 | 0 | 0 | + | 0 | -149.7213 | 0 | -149.7213 | 0
0 | 0 | 2039 |  | -450.8895 | 0 | 0 | + | 0 | -450.8895 | 0 | -450.8895 | 0
0 | 0 | 2040 |  | -742.3686 | 0 | 0 | + | 0 | -742.3686 | 0 | -742.3686 | 0
0 | 0 | 2041 |  | -271.2138 | 0 | 0 | + | 0 | -271.2138 | 0 | -271.2138 | 0
0 | 0 | 2042 |  | -674.7301 | 0 | 0 | + | 0 | -674.7301 | 0 | -674.7301 | 0
0 | 0 | 2043 |  | -237.4163 | 0 | 0 | + | 0 | -237.4163 | 0 | -237.4163 | 0
0 | 0 | 2044 |  | -639.2709 | 0 | 0 | + | 0 | -639.2709 | 0 | -639.2709 | 0
0 | 0 | 2045 |  | -164.7926 | 0 | 0 | + | 0 | -164.7926 | 0 | -164.7926 | 0
0 | 0 | 2046 |  | -564.9801 | 0 | 0 | + | 0 | -564.9801 | 0 | -564.9801 | 0
0 | 0 | 2047 |  | -88.8322 | 0 | 0 | + | 0 | -88.8322 | 0 | -88.8322 | 0
0 | 0 | 2048 |  | -487.3473 | 0 | 0 | + | 0 | -487.3473 | 0 | -487.3473 | 0
0 | 0 | 2049 |  | -9.5244 | 0 | 0 | + | 0 | -9.5244 | 0 | -9.5244 | 0
0 | 0 | 2050 |  | -346.3619 | 0 | 0 | + | 0 | -346.3619 | 0 | -346.3619 | 0
0 | 0 | 2051 |  | -742.3585 | 0 | 0 | + | 0 | -742.3585 | 0 | -742.3585 | 0
0 | 0 | 2052 |  | -262.013 | 0 | 0 | + | 0 | -262.013 | 0 | -262.013 | 0
0 | 0 | 2053 |  | -662.8811 | 0 | 0 | + | 0 | -662.8811 | 0 | -662.8811 | 0
0 | 0 | 2054 |  | -187.4419 | 0 | 0 | + | 0 | -187.4419 | 0 | -187.4419 | 0
0 | 0 | 2055 |  | -586.6941 | 0 | 0 | + | 0 | -586.6941 | 0 | -586.6941 | 0
0 | 0 | 2056 |  | -109.6366 | 0 | 0 | + | 0 | -109.6366 | 0 | -109.6366 | 0
0 | 0 | 2057 |  | -507.2683 | 0 | 0 | + | 0 | -507.2683 | 0 | -507.2683 | 0
0 | 0 | 2058 |  | -28.588 | 0 | 0 | + | 0 | -28.588 | 0 | -28.588 | 0
0 | 0 | 2059 |  | -424.5947 | 0 | 0 | + | 0 | -424.5947 | 0 | -424.5947 | 0
0 | 0 | 2060 |  | -819.7871 | 0 | 0 | + | 0 | -819.7871 | 0 | -819.7871 | 0
0 | 0 | 2061 |  | -338.6641 | 0 | 0 | + | 0 | -338.6641 | 0 | -338.6641 | 0
0 | 0 | 2062 |  | -732.2246 | 0 | 0 | + | 0 | -732.2246 | 0 | -732.2246 | 0
0 | 0 | 2063 |  | -249.4675 | 0 | 0 | + | 0 | -249.4675 | 0 | -249.4675 | 0
0 | 0 | 2064 |  | -637.7533 | 0 | 0 | + | 0 | -637.7533 | 0 | -637.7533 | 0
0 | 0 | 2065 |  | -206.0406 | 0 | 0 | + | 0 | -206.0406 | 0 | -206.0406 | 0

## Large Filler Calculations
0
Calculation of Large Filler Unit additions
[9 empty] | After Addition |  | After Addition |  | After Addition |  | After Addition |  | After Addition |  | After Addition |  | After Addition |  | After Addition |  | After Addition |  | After Addition |  | After Addition |  | After Addition |  | After Addition |  | After Addition |  | After Addition |  | After Addition |  | After Addition |  | After Addition |  | After Addition
Annual # of Large Fillers Added | # Large Filler(s) Added | Large Filler(s) (MW) | PPA (MW) | Year | Total New Unit MW | Need (MW) | Need For Years of Large Filler Additions | Large Filler(s) Added + PPA, if needed | Need For Years of Large Filler Additions | Large Filler(s) Added + PPA, if needed | Need For Years of Large Filler Additions | Large Filler(s) Added + PPA, if needed | Need For Years of Large Filler Additions | Large Filler(s) Added + PPA, if needed | Need For Years of Large Filler Additions | Large Filler(s) Added + PPA, if needed | Need For Years of Large Filler Additions | Large Filler(s) Added + PPA, if needed | Need For Years of Large Filler Additions | Large Filler(s) Added + PPA, if needed | Need For Years of Large Filler Additions | Large Filler(s) Added + PPA, if needed | Need For Years of Large Filler Additions | Large Filler(s) Added + PPA, if needed | Need For Years of Large Filler Additions | Large Filler(s) Added + PPA, if needed | Need For Years of Large Filler Additions | Large Filler(s) Added + PPA, if needed | Need For Years of Large Filler Additions | Large Filler(s) Added + PPA, if needed | Need For Years of Large Filler Additions | Large Filler(s) Added + PPA, if needed | Need For Years of Large Filler Additions | Large Filler(s) Added + PPA, if needed | Need For Years of Large Filler Additions | Large Filler(s) Added + PPA, if needed | Need For Years of Large Filler Additions | Large Filler(s) Added + PPA, if needed | Need For Years of Large Filler Additions | Large Filler(s) Added + PPA, if needed | Need For Years of Large Filler Additions | Large Filler(s) Added + PPA, if needed | Need For Years of Large Filler Additions | Large Filler(s) Added + PPA, if needed | Need For Years of Large Filler Additions
0 | 0 | 0 | 0 | 2016 | 0 | -445.3648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2017 | 0 | -0.47004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2018 | 0 | -0.21608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2019 | 0 | -1129.0885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2020 | 0 | -253.667 | -253.667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2021 | 0 | -502.9151 | -502.9151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2022 | 0 | -595.0431 | -595.0431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2023 | 0 | -479.7145 | -479.7145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2024 | 0 | -96.829 | -96.829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2025 | 0 | -0.01975 | -0.01975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2026 | 0 | -0.60585 | -0.60585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2027 | 0 | -1007.978 | -1007.978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2028 | 0 | -389.7841 | -389.7841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2029 | 0 | -0.95525 | -0.95525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2030 | 0 | 41.1982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2032 | 0 | -298.8468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2033 | 0 | -616.0119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2034 | 0 | -800.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2035 | 0 | -211.5429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2036 | 0 | -399.3738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2037 | 0 | -722.5584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2038 | 0 | -149.7213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2039 | 0 | -450.8895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2040 | 0 | -742.3686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2041 | 0 | -271.2138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2042 | 0 | -674.7301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2043 | 0 | -237.4163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2044 | 0 | -639.2709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2045 | 0 | -164.7926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2046 | 0 | -564.9801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2047 | 0 | -88.8322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2048 | 0 | -487.3473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2049 | 0 | -9.5244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2050 | 0 | -346.3619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2051 | 0 | -742.3585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2052 | 0 | -262.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2053 | 0 | -662.8811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2054 | 0 | -187.4419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2055 | 0 | -586.6941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2056 | 0 | -109.6366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2057 | 0 | -507.2683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2058 | 0 | -28.588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2059 | 0 | -424.5947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2060 | 0 | -819.7871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2061 | 0 | -338.6641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2062 | 0 | -732.2246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2063 | 0 | -249.4675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2064 | 0 | -637.7533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2065 | 0 | -206.0406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## NewUnit & Retire & ChngCap Name
2016 TYSP Update (ICL retired, only 60 MW ECOGEN, OCEC increase in MWs, and TP6 & 7 delayed to 2031 & 2032)
SUMMER
| UNIT ADDITIONS | [18 empty] | UNIT RETIREMENTS | [52 empty] | CAPACITY CHANGES OF UNITS
| Solar |  | Units Added |  | PPA |  | Large Filler |  |  |  | Small Filler |  |  |  | Eq Filler | [6 empty] | CCEC; | DeSoto Solar; | FM 2 CC; | FM 3A&3B CT; | FM GT; | FL 4; | FL 5; | PFL GT 1; |  | PFL GT 2; | MT 1; | MT 2; | MT 3; | MR 1; | MR 2; | MR 3; | MR 4; | MR 8; | PPE GT; |  | PN 1; | PN 2; | RBEC; | SN 4; | SN 5; | Scherer; | Space Coast Solar; | SJRPP 1; | SJRPP 2; | SL 1; |  | SL 2; |  | TP 1; |  | TP 2; | TP 3; |  | TP 4; |  | TP 5; | WCEC 1; | WCEC 2; | WCEC 3; | Cedar Bay; |  | Blank 2; | Blank 3; | Blank 4; | Blank 5; |  |  |  | CCEC; |  | DeSoto Solar; | FM 2 CC; | FM 3A&3B CT; |  | FM GT; |  | FL 4; | FL 5; | PFL GT 1; | PFL GT 2; |  | MT 1; | MT 2; | MT 3; |  | MR 1; | MR 2; | MR 3; |  | MR 4; |  | MR 8; |  | PPE GT; | PN 1; | PN 2; | RBEC; |  | SN 4; |  | SN 5; |  | Scherer; | Space Coast Solar; | SJRPP 1; | SJRPP 2; | SL 1; | SL 2; | TP 1; | TP 2; | TP 3; |  | TP 4; |  | TP 5; |  | WCEC 1; | WCEC 2; | WCEC 3; | Cedar Bay; | Blank 2; | Blank 3; | Blank 4; | Blank 5;
Year | MW | Name | MW | Name | MW | PPA | MW | MW | # of Units | GFCC | MW | MW | # of Units | Filler | MW | MW | Eq Filler | TOTAL TEXT | Year | [52 empty] | Year
2016 | 0 |  | 1237 | PEEC; | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  | PEEC; | 2016 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2016 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017 | 223.5 | 223.5 MW Solar; | 1617 | FM 2CT; PFL 5CT; | 53 | 53 MW PPA; | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  | 223.5 MW Solar; FM 2CT; PFL 5CT; 53 MW PPA; | 2017 | -1469.2 | PFL GT 1; PPE GT; TP 1; Cedar Bay; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411.6 | PFL GT 1; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411.6 | PPE GT; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 396 | TP 1; | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 250 | Cedar Bay; | 0 | 0 | 0 | 0 | 2017 | -773 | FM 3A&3B CT; FM GT; PFL GT 2; MT 3; MR 3; MR 4; MR 8; | 0 |  | 0 | 0 | 25 | FM 3A&3B CT; | -486 | FM GT; | 0 | 0 | 0 | -343 | PFL GT 2; | 0 | 0 | -8 | MT 3; | 0 | 0 | 29 | MR 3; | 14 | MR 4; | -4 | MR 8; | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018 | 0 |  | 0 |  | 324 | 324 MW PPA; | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  | 324 MW PPA; | 2018 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2018 | -19 | MT 3; SN 4; SN 5; TP 5; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | -2 | MT 3; | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | -1 | SN 4; | -1 | SN 5; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | -15 | TP 5; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019 | 0 |  | 1702 | OCEC; | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  | OCEC; | 2019 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2019 | 40 | TP 3; TP 4; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | TP 3; | 20 | TP 4; | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020 | 300 | 300 MW Solar; | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  | 300 MW Solar; | 2020 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2020 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 472 | 472 MW Solar; | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  | 472 MW Solar; | 2021 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2021 | 88 | CCEC; | 88 | CCEC; | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 471 | 471 MW Solar; | 45 | OCEC Inc MW; | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  | 471 MW Solar; OCEC Inc MW; | 2022 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2022 | 86 | RBEC; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 86 | RBEC; | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023 | 471 | 471 MW Solar; | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  | 471 MW Solar; | 2023 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2023 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  | 2024 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2024 | 2 | CCEC; | 2 | CCEC; | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025 | 0 |  | 255.35 | Battery; | 82 | 82 MW PPA; | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  | Battery; 82 MW PPA; | 2025 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2025 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026 | 0 |  | 550 | Battery; | 80 | 80 MW PPA; | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  | Battery; 80 MW PPA; | 2026 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2026 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027 | 0 |  | 1751 | CC; | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  | CC; | 2027 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2027 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2028 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  | 2028 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2028 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2029 | 0 |  | 200 | Battery; | 52 | 52 MW PPA; | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  | Battery; 52 MW PPA; | 2029 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2029 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2030 | 0 |  | 664.7 | Battery; | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  | Battery; | 2030 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2030 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 614.6176 | 614.6176 | 615 MW Eq Filler; | 615 MW Eq Filler; | 2031 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2031 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2032 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 1751 | 1751 | 2 | 2 Filler; | 614.6176 | 0 |  | 2 Filler; | 2032 | -831 | TP 3; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 831 | TP 3; | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2032 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2033 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 3502 | 1751 | 2 | 2 Filler; | 614.6176 | 0 |  | 2 Filler; | 2033 | -841 | TP 4; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 841 | TP 4; | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2033 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2034 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 4377.5 | 875.5 | 1 | 1 Filler; | 614.6176 | 0 |  | 1 Filler; | 2034 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2034 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2035 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 4377.5 | 0 | 0 |  | 614.6176 | 0 |  |  | 2035 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2035 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2036 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 6128.5 | 1751 | 2 | 2 Filler; | 614.6176 | 0 |  | 2 Filler; | 2036 | -981 | SL 1; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 981 | SL 1; | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2036 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2037 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 7004 | 875.5 | 1 | 1 Filler; | 614.6176 | 0 |  | 1 Filler; | 2037 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2037 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2038 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 7004 | 0 | 0 |  | 614.6176 | 0 |  |  | 2038 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2038 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2039 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 7879.5 | 875.5 | 1 | 1 Filler; | 614.6176 | 0 |  | 1 Filler; | 2039 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2039 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2040 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 8755 | 875.5 | 1 | 1 Filler; | 614.6176 | 0 |  | 1 Filler; | 2040 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2040 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2041 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 8755 | 0 | 0 |  | 614.6176 | 0 |  |  | 2041 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2041 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2042 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 9630.5 | 875.5 | 1 | 1 Filler; | 614.6176 | 0 |  | 1 Filler; | 2042 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2042 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2043 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 10506 | 875.5 | 1 | 1 Filler; | 614.6176 | 0 |  | 1 Filler; | 2043 | -840 | SL 2; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 840 | SL 2; | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2043 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2044 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 11381.5 | 875.5 | 1 | 1 Filler; | 614.6176 | 0 |  | 1 Filler; | 2044 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2044 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2045 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 11381.5 | 0 | 0 |  | 614.6176 | 0 |  |  | 2045 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2045 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2046 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 12257 | 875.5 | 1 | 1 Filler; | 614.6176 | 0 |  | 1 Filler; | 2046 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2046 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2047 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 12257 | 0 | 0 |  | 614.6176 | 0 |  |  | 2047 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2047 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2048 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 13132.5 | 875.5 | 1 | 1 Filler; | 614.6176 | 0 |  | 1 Filler; | 2048 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2048 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2049 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 13132.5 | 0 | 0 |  | 614.6176 | 0 |  |  | 2049 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2049 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2050 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 14008 | 875.5 | 1 | 1 Filler; | 614.6176 | 0 |  | 1 Filler; | 2050 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2050 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2051 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 14883.5 | 875.5 | 1 | 1 Filler; | 614.6176 | 0 |  | 1 Filler; | 2051 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2051 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2052 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 14883.5 | 0 | 0 |  | 614.6176 | 0 |  |  | 2052 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2052 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2053 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 15759 | 875.5 | 1 | 1 Filler; | 614.6176 | 0 |  | 1 Filler; | 2053 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2053 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2054 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 15759 | 0 | 0 |  | 614.6176 | 0 |  |  | 2054 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2054 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2055 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 16634.5 | 875.5 | 1 | 1 Filler; | 614.6176 | 0 |  | 1 Filler; | 2055 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2055 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2056 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 16634.5 | 0 | 0 |  | 614.6176 | 0 |  |  | 2056 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2056 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2057 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 17510 | 875.5 | 1 | 1 Filler; | 614.6176 | 0 |  | 1 Filler; | 2057 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2057 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2058 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 17510 | 0 | 0 |  | 614.6176 | 0 |  |  | 2058 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2058 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2059 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 18385.5 | 875.5 | 1 | 1 Filler; | 614.6176 | 0 |  | 1 Filler; | 2059 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2059 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2060 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 19261 | 875.5 | 1 | 1 Filler; | 614.6176 | 0 |  | 1 Filler; | 2060 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2060 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2061 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 19261 | 0 | 0 |  | 614.6176 | 0 |  |  | 2061 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2061 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2062 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 20136.5 | 875.5 | 1 | 1 Filler; | 614.6176 | 0 |  | 1 Filler; | 2062 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2062 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2063 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 20136.5 | 0 | 0 |  | 614.6176 | 0 |  |  | 2063 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2063 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2064 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 21012 | 875.5 | 1 | 1 Filler; | 614.6176 | 0 |  | 1 Filler; | 2064 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2064 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2065 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 21012 | 0 | 0 |  | 614.6176 | 0 |  |  | 2065 | 0 | ; | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2065 | 0 | ; | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## How to Use
Description of File Layout
"How to Use" tab (highlighted in red) describes the file layout and provides instructions on how to use.
There are four Input tabs highlighted in green, and require input for six different categories. Only the cells highlighted in light green are required input.
Input 1. Load, DSM, Cap Changes tab is used to input the Load Forecast (Section I), DSM plus incremental DSM projections (Section II) and any modifications to the
capacity of FPL's existing units that are not captured in the Input 3. Unit Capabiities-PGD tab. The first column in Section (III) is reserved for short-term unit outages
that are known to occur during the summer/winter peak months such as the 800 MW unit ESP outages.
"Input 2. Unit Additions" tab is used to input known future additions (e.g., PEEC in 2016, NPGU, future solar project, etc). Section IV, also, allows input of solar additions
with corresponding firm capacity value and degradation percent. Future filler additions are automatically added based on the input provided on rows 6 - 12. In order
to calculate these additions, inputs are needed regarding additions of PPA, large filler units, equalizing filler and small filler units. This tab also has an "Easy Button"
that must be pressed once all inputs have been completed.
Input 3. Unit Capabilities-PGD tab is used to input capacity of existing FPL units (Section V). This tab is formatted so that changes in inputs from one year to the next
are highlighted in yellow.
Input 4. Firm Capacity Purchase tab contains the inputs in Section VI. It is used to input all firm capacity from QFs, existing or future PPA contracts. This tab is
formatted so that changes in inputs from one year to the next are highlighted in yellow.
All output tabs (highlighted in blue) require no inputs and are protected.
Description of current output files …
How to Use
1. Input/update data in the four input tabs only in the green highlighted cells, as necessary.
2. Press the Easy Button on the Input 2. Unit Additions tab.

## Update Log
Reserve Margin Update Log
| Date | Person | Change
13 | 2016-07-28 | DI | Updated equalizing filler & small filler addition logic to work for situations were units are added after equalizing filler (such as TP 6 & 7)
12 | 2016-07-25 | DI | Updated TP 6 & 7 delay to 2031 and 2032, added 60 MW of ECOGEN with firm capacity in 2021 and updated OCEC capacity by 2022 of 1,747 MW
11 | 2016-05-11 | DI | Changes from 2016 TYSP: 1) ICL retires after the summer of 2019; 2) ECOGEN does not come on-line; and, 3) TP 6 & 7 are delayed to 2030 and 2031
10 | 2016-04-13 | DI | Added a tab with TYSP Schedule 7.1 extended beyond ten years
9 | 3/15/2016 | DI | Updated the capacity of the Greenfield CC from 1,633 MW to 1,622 MW
8 | 2016-03-01 | DI | Updated 2025 DSM values (per A. Sharma's email on March 1)
7 | 2016-02-26 | DI | Updated the dates for upgrades (20 MW) of Turkey Point 3 & 4; Per Alan Katz, scheduled for Fall 2018 (Unit 3) and Spring 2019 (Unit 4)
6 | 2016-02-17 | JE | Updated resource plan to show 2016 TYSP rsource plan - 300 MW of solar in 2020 and a 3x1 CC in 2024
5 | 2016-02-15 | DI | Updated the calculation for EGEAS reserve margin based on 10% GRM; Deleted the "Calculation" button and macro
4 | 2016-02-10 | DI | Ft. Myers GT retired December 31, 2016; therefore 594 MWs (54*11 MW) available for summer 2016 since GT #8 has already been retired
3 | 2016-02-09 | DI | Added an 100 MW Native load sale to TECO in 2016 (this is modeled under Section IV in "Input 4. Firm Purchase-Sale" tab)
2 | 2016-02-08 | DI | Updated DSM assumptions through 2030 (added additional columns for input of DSM assumptions)
Updated firm purchases: 1) removed Broward North, and 2) SJRPP Purchase available for summer 2019
Updated Greenfield filler capacity to 1,633 MW and small filler capacity to 817 MW
Updated Output 3. TYSP Table I.B.1 by removing excess rows under Cogeneration Small Power Production Facilities
1 | 2016-01-20 | DI | Updated model to begin in 2016
Updated 2016 DSM values (only) per A. Sharma

## Input 1. Load, DSM, Cap Changes
2016 TYSP Update (ICL retired, only 60 MW ECOGEN, OCEC increase in MWs, and TP6 & 7 delayed to 2031 & 2032) | [13 empty] | New Load Forecast with latest assumptions RM Spreadsheet upgrade test
|  |  |  | Title Description = | 2016 TYSP Update (ICL retired, only 60 MW ECOGEN, OCEC increase in MWs, and TP6 & 7 delayed to 2031 & 2032) | [13 empty] | Descriptive Title = | 2016 TYSP Update (ICL retired, only 60 MW ECOGEN, OCEC increase in MWs, and TP6 & 7 delayed to 2031 & 2032)
|  |  |  | Start Year = | 2016 | [13 empty] | Start Year = | 2016
|  |  |  | End Year = | 2046 | [13 empty] | End Year = | 2046
|  |  |  | Reserve Margin Criterion = | 20% | [13 empty] | Reserve Margin Criterion = | 20%
|  |  |  | Reserve Margin Criterion (Gen. Only) = | 10% | [5 empty] | Start Year of Gen Only RM Criterion = | 2019 | [6 empty] | Reserve Margin Criterion (Gen. Only) = | 10%
I. Load Forecast and Sales Forecast |  |  |  | II. DSM | [5 empty] | III. Existing FPL Capacity Modifications NOT CAPTURED in "Unit Capabilities PGD tab" |  |  |  | I. Load Forecast and Sales Forecast |  |  |  |  | II. DSM |  |  | III. Capacity Modifications (e.g., CT or nuclear uprates, retirements, outages, etc.); Negative values indicates loss of capacity
NOTE: First column is reserved for "Short Term Unit Outages (MW)" only. Negative value indicates loss of capacity.
SUMMER |  |  |  | SUMMER | [5 empty] | SUMMER |  |  |  | WINTER |  |  |  |  | WINTER |  |  | WINTER
| October 2015 Update | Sales Forecast (MW) | Sales Forecast (MW) |  | Conservation DSM at gen (MW) | Load Control DSM at gen (MW) | Incremental DSM 2026-2030 (MW) | Total DSM at gen (MW) | Projected Incremental DSM Year-Year (MW) |  | Short Term Unit Outages (MW) |  | Total (MW) |  | DRAFT "3" Forecast 10/14/14 WITHOUT VERO (MW) | Sales Forecast (MW) | Sales Forecast (MW) |  |  | DSM Capability (MW) | Assumed Additional DSM (MW) |  | Unit Upgrades - CT (MW) | Incremental Units from Wholesale Purchases (e.g.,Vero Units) MW | Units Converted to Syn Condensor | Short Term Unit Outages (MW) | Reitrement of Existing Nuclear (MW) | Other Retirements / Units on Inactive Reserve (MW) | Other (MW) | Other (MW) | Total (MW)
August |  |  |  | August |  | Load Control |  |  |  | August |  |  |  | Jan |  |  |  |  | Jan |  |  | Jan
of the |  |  |  | of the |  | DSM at gen |  |  |  | of the |  |  |  | of the |  |  |  |  | of the |  |  | of the
Year |  |  |  | Year |  | (MW) |  |  |  | Year |  |  |  | Year |  |  |  |  | Year |  |  | Year
2016 | 24169.6865 | 0 | 0 | 2016 | 52.1053 | 1790.3613 | 0 | 1842.4667 | 0 | 2016 | 0 |  | 0 | 2016 | 22768.3999 | 0 | 0 |  | 2016 | 1893.4319 | 98.4098 | 2016 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38
2017 | 24336.0406 | 0 | 0 | 2017 | 80.5244 | 1854.2805 | 0 | 1934.8049 | 92.3382 | 2017 | 0 |  | 0 | 2017 | 23355.5765 | 0 | 0 | 1 | 2017 | 1899.7488 | 157.9386 | 2017 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123
2018 | 24606.279 | 0 | 0 | 2018 | 105.0481 | 1890.1534 | 0 | 1995.2014 | 60.3965 | 2018 | 0 |  | 0 | 2018 | 23777.7076 | 0 | 0 | 2 | 2018 | 1895.041 | 187.6774 | 2018 | 123 | 0 | 0 | 0 | 0 | -498 | 0 | 0 | -375
2019 | 24893.0945 | 0 | 0 | 2019 | 130.3217 | 1911.124 | 0 | 2041.4457 | 46.2443 | 2019 | 0 |  | 0 | 2019 | 24190.1254 | 0 | 0 | 3 | 2019 | 1890.3682 | 218.8841 | 2019 | 123 | 0 | -392 | 0 | 0 | -498 | 0 | 0 | -767
2020 | 25205.9285 | 0 | 0 | 2020 | 156.4111 | 1932.0511 | 0 | 2088.4622 | 47.0165 | 2020 | 0 |  | 0 | 2020 | 24543.7588 | 0 | 0 | 4 | 2020 | 1885.7293 | 251.3967 | 2020 | 123 | 0 | -392 | 0 | 0 | -498 | 0 | 0 | -767
2021 | 25316.4163 | 0 | 0 | 2021 | 183.3005 | 1952.9339 | 0 | 2136.2343 | 47.7721 | 2021 | 0 |  | 0 | 2021 | 24895.5689 | 0 | 0 | 5 | 2021 | 1881.1231 | 285.7636 | 2021 | 123 | 0 | -392 | 0 | 0 | -498 | 0 | 0 | -767
2022 | 25540.1892 | 0 | 0 | 2022 | 210.9741 | 1973.7724 | 0 | 2184.7465 | 48.5122 | 2022 | 0 |  | 0 | 2022 | 25239.3053 | 0 | 0 | 6 | 2022 | 1876.5496 | 320.6839 | 2022 | 123 | 0 | -392 | 0 | 0 | -498 | 0 | 0 | -767
2023 | 25832.9033 | 0 | 0 | 2023 | 239.4635 | 1994.566 | 0 | 2234.0295 | 49.283 | 2023 | 0 |  | 0 | 2023 | 25438.8452 | 0 | 0 | 7 | 2023 | 1872.0077 | 356.2604 | 2023 | 123 | 0 | -392 | 0 | 0 | -498 | 0 | 0 | -767
2024 | 26180.2785 | 0 | 0 | 2024 | 268.8685 | 2015.3137 | 0 | 2284.1822 | 50.1527 | 2024 | 0 |  | 0 | 2024 | 25907.6411 | 0 | 0 | 8 | 2024 | 1867.4962 | 392.6438 | 2024 | 123 | 0 | -392 | 0 | 0 | -498 | 0 | 0 | -767
2025 | 26572.456 | 0 | 0 | 2025 | 299 | 2035 | 0 | 2334 | 49.8178 | 2025 | 0 |  | 0 | 2025 | 26528.2942 | 0 | 0 | 9 | 2025 | 1863.2603 | 429.9727 | 2025 | 123 | 0 | -392 | 0 | 0 | -498 | 0 | 0 | -767
2026 | 27067.6001 | 0 | 0 | 2026 | 299 | 2035 | 50 | 2384 | 50 | 2026 | 0 |  | 0 | 2026 | 27214.2486 | 0 | 0 | 10 | 2026 | 1859.0779 | 468.4615 | 2026 | 123 | 0 | -392 | 0 | 0 | -498 | 0 | 0 | -767
2027 | 27665.2192 | 0 | 0 | 2027 | 299 | 2035 | 100 | 2434 | 50 | 2027 | 0 |  | 0 | 2027 | 27877.1239 | 0 | 0 | 11 | 2027 | 1854.9123 | 468.4615 | 2027 | 123 | 0 | -392 | 0 | 0 | -498 | 0 | 0 | -767
2028 | 28224.7243 | 0 | 0 | 2028 | 299 | 2035 | 150 | 2484 | 50 | 2028 | 0 |  | 0 | 2028 | 28504.646 | 0 | 0 | 12 | 2028 | 1850.7636 | 468.4615 | 2028 | 123 | 0 | -392 | 0 | 0 | -498 | 0 | 0 | -767
2029 | 28804.8144 | 0 | 0 | 2029 | 299 | 2035 | 200 | 2534 | 50 | 2029 | 0 |  | 0 | 2029 | 29134.6314 | 0 | 0 | 13 | 2029 | 1850.7636 | 468.4615 | 2029 | 123 | 0 | -392 | 0 | 0 | -498 | 0 | 0 | -767
2030 | 29397.6618 | 0 | 0 | 2030 | 299 | 2035 | 250 | 2584 | 50 | 2030 | 0 |  | 0 | 2030 | 29731.1329 | 0 | 0 | 14 | 2030 | 1850.7636 | 468.4615 | 2030 | 123 | 0 | -392 | 0 | 0 | -498 | 0 | 0 | -767
2031 | 29916.486 | 0 | 0 | 2031 | 299 | 2035 | 250 | 2584 | 0 | 2031 | 0 |  | 0 | 2031 | 30260.6981 | 0 | 0 | 15 | 2031 | 1850.7636 | 468.4615 | 2031 | 123 | 0 | -392 | 0 | 0 | -498 | 0 | 0 | -767
2032 | 30478.7122 | 0 | 0 | 2032 | 299 | 2035 | 250 | 2584 | 0 | 2032 | 0 |  | 0 | 2032 | 30785.51 | 0 | 0 | 16 | 2032 | 1850.7636 | 468.4615 | 2032 | 123 | 0 | -392 | 0 | -811 | -498 | 0 | 0 | -1578
2033 | 31014.602 | 0 | 0 | 2033 | 299 | 2035 | 250 | 2584 | 0 | 2033 | 0 |  | 0 | 2033 | 31332.208 | 0 | 0 | 17 | 2033 | 1850.7636 | 468.4615 | 2033 | 123 | 0 | -392 | 0 | -1632 | -498 | 0 | 0 | -2399
2034 | 31496.9298 | 0 | 0 | 2034 | 299 | 2035 | 250 | 2584 | 0 | 2034 | 0 |  | 0 | 2034 | 31881.4572 | 0 | 0 | 18 | 2034 | 1850.7636 | 468.4615 | 2034 | 123 | 0 | -392 | 0 | -1632 | -498 | 0 | 0 | -2399
2035 | 31985.1039 | 0 | 0 | 2035 | 299 | 2035 | 250 | 2584 | 0 | 2035 | 0 |  | 0 | 2035 | 32402.8578 | 0 | 0 | 19 | 2035 | 1850.7636 | 468.4615 | 2035 | 123 | 0 | -392 | 0 | -1632 | -498 | 0 | 0 | -2399
2036 | 32468.0191 | 0 | 0 | 2036 | 299 | 2035 | 250 | 2584 | 0 | 2036 | 0 |  | 0 | 2036 | 32928.3325 | 0 | 0 | 20 | 2036 | 1850.7636 | 468.4615 | 2036 | 123 | 0 | -392 | 0 | -2613 | -498 | 0 | 0 | -3380
2037 | 32926.0632 | 0 | 0 | 2037 | 299 | 2035 | 250 | 2584 | 0 | 2037 | 0 |  | 0 | 2037 | 33444.1233 | 0 | 0 | 21 | 2037 | 1850.7636 | 468.4615 | 2037 | 123 | 0 | -392 | 0 | -2613 | -498 | 0 | 0 | -3380
2038 | 33401.2155 | 0 | 0 | 2038 | 299 | 2035 | 250 | 2584 | 0 | 2038 | 0 |  | 0 | 2038 | 33942.4433 | 0 | 0 | 22 | 2038 | 1850.7636 | 468.4615 | 2038 | 123 | 0 | -392 | 0 | -2613 | -498 | 0 | 0 | -3380
2039 | 33877.6204 | 0 | 0 | 2039 | 299 | 2035 | 250 | 2584 | 0 | 2039 | 0 |  | 0 | 2039 | 34413.4745 | 0 | 0 | 23 | 2039 | 1850.7636 | 468.4615 | 2039 | 123 | 0 | -392 | 0 | -2613 | -498 | 0 | 0 | -3380
2040 | 34362.1064 | 0 | 0 | 2040 | 299 | 2035 | 250 | 2584 | 0 | 2040 | 0 |  | 0 | 2040 | 34927.6239 | 0 | 0 | 24 | 2040 | 1850.7636 | 468.4615 | 2040 | 123 | 0 | -392 | 0 | -2613 | -498 | 0 | 0 | -3380
2041 | 34752.544 | 0 | 0 | 2041 | 299 | 2035 | 250 | 2584 | 0 | 2041 | 0 |  | 0 | 2041 | 35445.3868 | 0 | 0 | 25 | 2041 | 1850.7636 | 468.4615 | 2041 | 123 | 0 | -392 | 0 | -2613 | -498 | 0 | 0 | -3380
2042 | 35143.6793 | 0 | 0 | 2042 | 299 | 2035 | 250 | 2584 | 0 | 2042 | 0 |  | 0 | 2042 | 35956.6479 | 0 | 0 | 26 | 2042 | 1850.7636 | 468.4615 | 2042 | 123 | 0 | -392 | 0 | -2613 | -498 | 0 | 0 | -3380
2043 | 35535.5131 | 0 | 0 | 2043 | 299 | 2035 | 250 | 2584 | 0 | 2043 | 0 |  | 0 | 2043 | 36301.7011 | 0 | 0 | 27 | 2043 | 1850.7636 | 468.4615 | 2043 | 123 | 0 | -392 | 0 | -3453 | -498 | 0 | 0 | -4220
2044 | 35928.0467 | 0 | 0 | 2044 | 299 | 2035 | 250 | 2584 | 0 | 2044 | 0 |  | 0 | 2044 | 36650.0903 | 0 | 0 | 28 | 2044 | 1850.7636 | 468.4615 | 2044 | 123 | 0 | -392 | 0 | -3453 | -498 | 0 | 0 | -4220
2045 | 36321.2811 | 0 | 0 | 2045 | 299 | 2035 | 250 | 2584 | 0 | 2045 | 0 |  | 0 | 2045 | 37001.8537 | 0 | 0 | 29 | 2045 | 1850.7636 | 468.4615 | 2045 | 123 | 0 | -392 | 0 | -3453 | -498 | 0 | 0 | -4220
2046 | 36715.2173 | 0 | 0 | 2046 | 299 | 2035 | 250 | 2584 | 0 | 2046 | 0 |  | 0 | 2046 | 37357.0245 | 0 | 0 | 30 | 2046 | 1850.7636 | 468.4615 | 2046 | 123 | 0 | -392 | 0 | -3453 | -498 | 0 | 0 | -4220
2047 | 37109.8565 | 0 | 0 | 2047 | 299 | 2035 | 250 | 2584 | 0 | 2047 | 0 |  | 0 | 2047 | 37715.6359 | 0 | 0 | 31 | 2047 | 1850.7636 | 468.4615 | 2047 | 123 | 0 | -392 | 0 | -3453 | -498 | 0 | 0 | -4220
2048 | 37505.1998 | 0 | 0 | 2048 | 299 | 2035 | 250 | 2584 | 0 | 2048 | 0 |  | 0 | 2048 | 38077.7214 | 0 | 0 | 32 | 2048 | 1850.7636 | 468.4615 | 2048 | 123 | 0 | -392 | 0 | -3453 | -498 | 0 | 0 | -4220
2049 | 37901.2482 | 0 | 0 | 2049 | 299 | 2035 | 250 | 2584 | 0 | 2049 | 0 |  | 0 | 2049 | 38443.315 | 0 | 0 | 33 | 2049 | 1850.7636 | 468.4615 | 2049 | 123 | 0 | -392 | 0 | -3453 | -498 | 0 | 0 | -4220
2050 | 38298.0028 | 0 | 0 | 2050 | 299 | 2035 | 250 | 2584 | 0 | 2050 | 0 |  | 0 | 2050 | 38812.451 | 0 | 0 | 34 | 2050 | 1850.7636 | 468.4615 | 2050 | 123 | 0 | -392 | 0 | -3453 | -498 | 0 | 0 | -4220
2051 | 38695.4648 | 0 | 0 | 2051 | 299 | 2035 | 250 | 2584 | 0 | 2051 | 0 |  | 0 | 2051 | 39185.1638 | 0 | 0 | 35 | 2051 | 1850.7636 | 468.4615 | 2051 | 123 | 0 | -392 | 0 | -3453 | -498 | 0 | 0 | -4220
2052 | 39093.6352 | 0 | 0 | 2052 | 299 | 2035 | 250 | 2584 | 0 | 2052 | 0 |  | 0 | 2052 | 39561.4883 | 0 | 0 | 36 | 2052 | 1850.7636 | 468.4615 | 2052 | 123 | 0 | -392 | 0 | -3453 | -498 | 0 | 0 | -4220
2053 | 39487.0507 | 0 | 0 | 2053 | 299 | 2035 | 250 | 2584 | 0 | 2053 | 0 |  | 0 | 2053 | 39941.4598 | 0 | 0 | 37 | 2053 | 1850.7636 | 468.4615 | 2053 | 123 | 0 | -392 | 0 | -3453 | -498 | 0 | 0 | -4220
2054 | 39881.1457 | 0 | 0 | 2054 | 299 | 2035 | 250 | 2584 | 0 | 2054 | 0 |  | 0 | 2054 | 40325.1139 | 0 | 0 | 38 | 2054 | 1850.7636 | 468.4615 | 2054 | 123 | 0 | -392 | 0 | -3453 | -498 | 0 | 0 | -4220
2055 | 40275.9209 | 0 | 0 | 2055 | 299 | 2035 | 250 | 2584 | 0 | 2055 | 0 |  | 0 | 2055 | 40704.5439 | 0 | 0 | 39 | 2055 | 1850.7636 | 468.4615 | 2055 | 123 | 0 | -392 | 0 | -3453 | -498 | 0 | 0 | -4220
2056 | 40671.3775 | 0 | 0 | 2056 | 299 | 2035 | 250 | 2584 | 0 | 2056 | 0 |  | 0 | 2056 | 41087.6691 | 0 | 0 | 40 | 2056 | 1850.7636 | 468.4615 | 2056 | 123 | 0 | -392 | 0 | -3453 | -498 | 0 | 0 | -4220
2057 | 41067.5161 | 0 | 0 | 2057 | 299 | 2035 | 250 | 2584 | 0 | 2057 | 0 |  | 0 | 2057 | 41474.5256 | 0 | 0 | 41 | 2057 | 1850.7636 | 468.4615 | 2057 | 123 | 0 | -392 | 0 | -3453 | -498 | 0 | 0 | -4220
2058 | 41464.3379 | 0 | 0 | 2058 | 299 | 2035 | 250 | 2584 | 0 | 2058 | 0 |  | 0 | 2058 | 41865.1499 | 0 | 0 | 42 | 2058 | 1850.7636 | 468.4615 | 2058 | 123 | 0 | -392 | 0 | -3453 | -498 | 0 | 0 | -4220
2059 | 41861.8437 | 0 | 0 | 2059 | 299 | 2035 | 250 | 2584 | 0 | 2059 | 0 |  | 0 | 2059 | 42259.5789 | 0 | 0 | 43 | 2059 | 1850.7636 | 468.4615 | 2059 | 123 | 0 | -392 | 0 | -3453 | -498 | 0 | 0 | -4220
2060 | 42260.0345 | 0 | 0 | 2060 | 299 | 2035 | 250 | 2584 | 0 | 2060 | 0 |  | 0 | 2060 | 42657.8498 | 0 | 0 | 44 | 2060 | 1850.7636 | 468.4615 | 2060 | 123 | 0 | -392 | 0 | -3453 | -498 | 0 | 0 | -4220
2061 | 42658.9112 | 0 | 0 | 2061 | 299 | 2035 | 250 | 2584 | 0 | 2061 | 0 |  | 0 | 2061 | 43060.0003 | 0 | 0 | 45 | 2061 | 1850.7636 | 468.4615 | 2061 | 123 | 0 | -392 | 0 | -3453 | -498 | 0 | 0 | -4220
2062 | 43058.4746 | 0 | 0 | 2062 | 299 | 2035 | 250 | 2584 | 0 | 2062 | 0 |  | 0 | 2062 | 43466.0683 | 0 | 0 | 46 | 2062 | 1850.7636 | 468.4615 | 2062 | 123 | 0 | -392 | 0 | -3453 | -498 | 0 | 0 | -4220
2063 | 43458.7259 | 0 | 0 | 2063 | 299 | 2035 | 250 | 2584 | 0 | 2063 | 0 |  | 0
2064 | 43862.6977 | 0 | 0 | 2064 | 299 | 2035 | 250 | 2584 | 0 | 2064 | 0 |  | 0
2065 | 44270.4246 | 0 | 0 | 2065 | 299 | 2035 | 300 | 2634 | 50 | 2065 | 0 |  | 0

## Input 2. Unit Additions
2016 TYSP Update (ICL retired, only 60 MW ECOGEN, OCEC increase in MWs, and TP6 & 7 delayed to 2031 & 2032)
SUMMER
[5 empty] | Solar Degradation = | 0.3%
|  | PPA Data Input: |  |  | Add Short-Term PPA up to Need Amount = | 200 |  |  |  |  | Add PPA (as only option available) up to the need prior to = | 2020
|  | Large Filler Input: | Start Year = | 2020 | End Year = | 2029 |  |  |  |  | Summer Capacity (MW) = | 1751
|  | Equalizing Filler Input: |  |  | Do you want to add an Equalizing Filler (Yes/No) = | Yes |  | Year of Equalizing Filler = | 2031
|  | Small Filler Input: | Start Year = | 2032 | [6 empty] | Summer Capacity (MW) = | 875.5
IV. New Capacity Additions
| Nameplate AC Solar Addition (MW) | Firm Capacity Value | Description of Unit Additions | New Unit Additions (MW) | Short Term PPA (MW) | Large Filler (e.g., 3x1 J CC) Additions (MW) | Small Filler (e.g., 1/2 the size of 3x1 J CC) Additions (MW) | Equalizing Filler (MW) | Total (MW) |  | Reserve Margin Criterion 20 % | MW Needed to Meet Reserve Margin | Reserve Margin Generation Only Criterion 10 % | MW Needed to Meet Generation Only Reserve Margin | Reserve Margin Check |  | Short Term PPA (MW) | Large Filler (e.g., 3x1 J CC) Additions (MW) | Small Filler (e.g., 1/2 the size of 3x1 J CC) Additions (MW) | Equalizing Filler (MW) | Total (MW)
August |  |  |  | New Unit | [5 empty] | Aug | [5 empty] | August
of the |  |  |  | Additions | [5 empty] | of the | [5 empty] | of the
Year |  |  |  | (MW) | [5 empty] | Year | [5 empty] | Year
2016 |  |  | PEEC | 1237 | 0 | 0 | 0 | 0 | 1237 | 2016 | 21.99% | -445.3648 |  |  | OK | 2016 | 0 | 0 | 0 | 0 | 1237
2017 | 223.5 | 52% | FM 2CT; PFL 5CT | 1617 | 53 | 0 | 0 | 0 | 3023.22 | 2017 | 20% | -0.47004 |  |  | OK | 2017 | 0 | 0 | 0 | 0 | 3023.22
2018 |  |  |  |  | 324 | 0 | 0 | 0 | 3293.8713 | 2018 | 20% | -0.21608 |  |  | OK | 2018 | 0 | 0 | 0 | 0 | 3293.8713
2019 |  |  | OCEC | 1702 | 0 | 0 | 0 | 0 | 4671.5237 | 2019 | 24.94% | -1129.0885 | 14.69% | -1168.6631 | OK | 2019 | 0 | 0 | 0 | 0 | 4671.5237
2020 | 300 | 52% | Unsited Solar |  | 0 | 0 | 0 | 0 | 4827.1772 | 2020 | 21.1% | -253.667 | 11.06% | -268.1052 | OK | 2020 | 0 | 0 | 0 | 0 | 4827.1772
2021 | 472 | 44.33% |  |  | 0 | 0 | 0 | 0 | 5035.6168 | 2021 | 22.31% | -534.7546 | 11.99% | -502.9151 | OK | 2021 | 0 | 0 | 0 | 0 | 5035.6168
2022 | 471 | 44.33% | OCEC Inc MW | 45 | 0 | 0 | 0 | 0 | 5287.9878 | 2022 | 22.84% | -662.72 | 12.33% | -595.0431 | OK | 2022 | 0 | 0 | 0 | 0 | 5287.9878
2023 | 471 | 44.33% |  |  | 0 | 0 | 0 | 0 | 5494.7367 | 2023 | 22.45% | -577.2596 | 11.86% | -479.7145 | OK | 2023 | 0 | 0 | 0 | 0 | 5494.7367
2024 |  |  |  |  | 0 | 0 | 0 | 0 | 5492.0555 | 2024 | 20.92% | -219.8198 | 10.37% | -96.829 | OK | 2024 | 0 | 0 | 0 | 0 | 5492.0555
2025 |  |  | Battery | 255.35 | 82 | 0 | 0 | 0 | 5826.7323 | 2025 | 20.59% | -143.5741 | 10% | -0.01975 | OK | 2025 | 0 | 0 | 0 | 0 | 5826.7323
2026 |  |  | Battery | 550 | 80 | 0 | 0 | 0 | 6372.0671 | 2026 | 20.63% | -154.6458 | 10% | -0.60585 | OK | 2026 | 0 | 0 | 0 | 0 | 6372.0671
2027 |  |  | CC | 1751 | 0 | 0 | 0 | 0 | 8040.41 | 2027 | 24.61% | -1162.2561 | 13.64% | -1007.978 | OK | 2027 | 0 | 0 | 0 | 0 | 8040.41
2028 |  |  |  |  | 0 | 0 | 0 | 0 | 8037.7608 | 2028 | 22.13% | -548.1116 | 11.38% | -389.7841 | OK | 2028 | 0 | 0 | 0 | 0 | 8037.7608
2029 |  |  | Battery | 200 | 52 | 0 | 0 | 0 | 8287.1196 | 2029 | 20.61% | -161.2738 | 10% | -0.95525 | OK | 2029 | 0 | 0 | 0 | 0 | 8287.1196
2030 |  |  | Battery | 664.7 | 0 | 0 | 0 | 0 | 8897.1863 | 2030 | 20.45% | -119.8356 | 9.86% | 41.1982 | OK | 2030 | 0 | 0 | 0 | 0 | 8897.1863
2031 |  |  |  |  | 0 | 0 | 0 | 614.6176 | 9509.1785 | 2031 | 20.4% | -109.1514 | 10% | 0 | OK | 2031 | 0 | 0 | 0 | 0 | 9509.1785
2032 |  |  |  |  | 0 | 0 | 1751 | 614.6176 | 11257.5609 | 2032 | 21.26% | -351.7756 | 10.98% | -298.8468 | OK | 2032 | 0 | 0 | 0 | 0 | 11257.5609
2033 |  |  |  |  | 0 | 0 | 3502 | 614.6176 | 13005.9513 | 2033 | 22.17% | -616.0119 | 11.99% | -616.6721 | OK | 2033 | 0 | 0 | 0 | 0 | 13005.9513
2034 |  |  |  |  | 0 | 0 | 4377.5 | 614.6176 | 13878.8494 | 2034 | 22.77% | -800.031 | 12.7% | -848.924 | OK | 2034 | 0 | 0 | 0 | 0 | 13878.8494
2035 |  |  |  |  | 0 | 0 | 4377.5 | 614.6176 | 13876.2554 | 2035 | 20.72% | -211.5429 | 10.97% | -309.2533 | OK | 2035 | 0 | 0 | 0 | 0 | 13876.2554
2036 |  |  |  |  | 0 | 0 | 6128.5 | 614.6176 | 15624.6691 | 2036 | 21.34% | -399.3738 | 11.68% | -545.3758 | OK | 2036 | 0 | 0 | 0 | 0 | 15624.6691
2037 |  |  |  |  | 0 | 0 | 7004 | 614.6176 | 16497.5906 | 2037 | 22.38% | -722.5584 | 12.78% | -914.3647 | OK | 2037 | 0 | 0 | 0 | 0 | 16497.5906
2038 |  |  |  |  | 0 | 0 | 7004 | 614.6176 | 16495.0198 | 2038 | 20.49% | -149.7213 | 11.16% | -389.0429 | OK | 2038 | 0 | 0 | 0 | 0 | 16495.0198
2039 |  |  |  |  | 0 | 0 | 7879.5 | 614.6176 | 17367.9568 | 2039 | 21.44% | -450.8895 | 12.18% | -737.8516 | OK | 2039 | 0 | 0 | 0 | 0 | 17367.9568
2040 |  |  |  |  | 0 | 0 | 8755 | 614.6176 | 18240.9014 | 2040 | 22.34% | -742.3686 | 13.14% | -1077.7792 | OK | 2040 | 0 | 0 | 0 | 0 | 18240.9014
2041 |  |  |  |  | 0 | 0 | 8755 | 614.6176 | 18238.3537 | 2041 | 20.84% | -271.2138 | 11.86% | -645.6682 | OK | 2041 | 0 | 0 | 0 | 0 | 18238.3537
2042 |  |  |  |  | 0 | 0 | 9630.5 | 614.6176 | 19111.3136 | 2042 | 22.07% | -674.7301 | 13.1% | -1088.2981 | OK | 2042 | 0 | 0 | 0 | 0 | 19111.3136
2043 |  |  |  |  | 0 | 0 | 10506 | 614.6176 | 19984.2812 | 2043 | 20.72% | -237.4163 | 11.94% | -690.1676 | OK | 2043 | 0 | 0 | 0 | 0 | 19984.2812
2044 |  |  |  |  | 0 | 0 | 11381.5 | 614.6176 | 20857.2564 | 2044 | 21.92% | -639.2709 | 13.15% | -1131.2755 | OK | 2044 | 0 | 0 | 0 | 0 | 20857.2564
2045 |  |  |  |  | 0 | 0 | 11381.5 | 614.6176 | 20854.7391 | 2045 | 20.49% | -164.7926 | 11.92% | -696.1207 | OK | 2045 | 0 | 0 | 0 | 0 | 20854.7391
2046 |  |  |  |  | 0 | 0 | 12257 | 614.6176 | 21727.7294 | 2046 | 21.66% | -564.9801 | 13.09% | -1135.7019 | OK | 2046 | 0 | 0 | 0 | 0 | 21727.7294
2047 |  |  |  |  | 0 | 0 | 12257 | 614.6176 | 21725.2272 | 2047 | 20.26% | -88.8322 | 11.88% | -699.0178 | OK | 2047 | 0 | 0 | 0 | 0 | 21725.2272
2048 |  |  |  |  | 0 | 0 | 13132.5 | 614.6176 | 22598.2325 | 2048 | 21.4% | -487.3473 | 13.03% | -1137.0673 | OK | 2048 | 0 | 0 | 0 | 0 | 22598.2325
2049 |  |  |  |  | 0 | 0 | 13132.5 | 614.6176 | 22595.7453 | 2049 | 20.03% | -9.5244 | 11.84% | -698.8492 | OK | 2049 | 0 | 0 | 0 | 0 | 22595.7453
2050 |  |  |  |  | 0 | 0 | 14008 | 614.6176 | 23468.7656 | 2050 | 20.97% | -346.3619 | 12.81% | -1075.3621 | OK | 2050 | 0 | 0 | 0 | 0 | 23468.7656
2051 |  |  |  |  | 0 | 0 | 14883.5 | 614.6176 | 24341.7933 | 2051 | 22.06% | -742.3585 | 13.91% | -1511.105 | OK | 2051 | 0 | 0 | 0 | 0 | 24341.7933
2052 |  |  |  |  | 0 | 0 | 14883.5 | 614.6176 | 24339.3284 | 2052 | 20.72% | -262.013 | 12.74% | -1070.5765 | OK | 2052 | 0 | 0 | 0 | 0 | 24339.3284
2053 |  |  |  |  | 0 | 0 | 15759 | 614.6176 | 25212.3709 | 2053 | 21.8% | -662.8811 | 13.83% | -1510.7862 | OK | 2053 | 0 | 0 | 0 | 0 | 25212.3709
2054 |  |  |  |  | 0 | 0 | 15759 | 614.6176 | 25209.9208 | 2054 | 20.5% | -187.4419 | 12.69% | -1074.7564 | OK | 2054 | 0 | 0 | 0 | 0 | 25209.9208
2055 |  |  |  |  | 0 | 0 | 16634.5 | 614.6176 | 26082.9781 | 2055 | 21.56% | -586.6941 | 13.76% | -1513.4862 | OK | 2055 | 0 | 0 | 0 | 0 | 26082.9781
2056 |  |  |  |  | 0 | 0 | 16634.5 | 614.6176 | 26080.5426 | 2056 | 20.29% | -109.6366 | 12.65% | -1075.9743 | OK | 2056 | 0 | 0 | 0 | 0 | 26080.5426
2057 |  |  |  |  | 0 | 0 | 17510 | 614.6176 | 26953.6145 | 2057 | 21.32% | -507.2683 | 13.68% | -1513.2199 | OK | 2057 | 0 | 0 | 0 | 0 | 26953.6145
2058 |  |  |  |  | 0 | 0 | 17510 | 614.6176 | 26951.1937 | 2058 | 20.07% | -28.588 | 12.59% | -1074.2218 | OK | 2058 | 0 | 0 | 0 | 0 | 26951.1937
2059 |  |  |  |  | 0 | 0 | 18385.5 | 614.6176 | 27824.2801 | 2059 | 21.08% | -424.5947 | 13.61% | -1509.979 | OK | 2059 | 0 | 0 | 0 | 0 | 27824.2801
2060 |  |  |  |  | 0 | 0 | 19261 | 614.6176 | 28697.3737 | 2060 | 22.07% | -819.7871 | 14.6% | -1944.9905 | OK | 2060 | 0 | 0 | 0 | 0 | 28697.3737
2061 |  |  |  |  | 0 | 0 | 19261 | 614.6176 | 28694.9746 | 2061 | 20.85% | -338.6641 | 13.53% | -1503.7552 | OK | 2061 | 0 | 0 | 0 | 0 | 28694.9746
2062 |  |  |  |  | 0 | 0 | 20136.5 | 614.6176 | 29568.0827 | 2062 | 21.81% | -732.2246 | 14.5% | -1937.2721 | OK | 2062 | 0 | 0 | 0 | 0 | 29568.0827
2063 |  |  |  |  | 0 | 0 | 20136.5 | 614.6176 | 29565.698 | 2063 | 20.61% | -249.4675 | 13.44% | -1494.5401 | OK | 2063 | 0 | 0 | 0 | 0 | 29565.698
2064 |  |  |  |  | 0 | 0 | 21012 | 614.6176 | 30438.8204 | 2064 | 21.54% | -637.7533 | 14.38% | -1923.2231 | OK | 2064 | 0 | 0 | 0 | 0 | 30438.8204
2065 |  |  |  |  | 0 | 0 | 21012 | 614.6176 | 30436.4499 | 2065 | 20.49% | -206.0406 | 13.33% | -1472.283 | OK | 2065 | 0 | 0 | 0 | 0 | 30436.4499
Easy Button

## Input 3. Unit Capabilities-PGD
2016 TYSP Update (ICL retired, only 60 MW ECOGEN, OCEC increase in MWs, and TP6 & 7 delayed to 2031 & 2032)
V. Existing Unit Capability |  |  |  |  | Indicates change in capacity from one year to the next | [23 empty] | Indicates change in capacity from one year to the next
SUMMER
| Unit Name | CCEC | DeSoto Solar | FM 2 CC | FM 3A&3B CT | FM GT | FL 4 | FL 5 | PFL GT 1 | PFL GT 2 | MT 1 | MT 2 | MT 3 | MR 1 | MR 2 | MR 3 | MR 4 | MR 8 | PPE GT | PN 1 | PN 2 | RBEC | SN 4 | SN 5 | Scherer | Space Coast Solar | SJRPP 1 | SJRPP 2 | SL 1 | SL 2 | TP 1 | TP 2 | TP 3 | TP 4 | TP 5 | WCEC 1 | WCEC 2 | WCEC 3 | Cedar Bay | Blank 2 | Blank 3 | Blank 4 | Blank 5
Year | Total Existing Unit Capacity (MW)
2016 | 25275.5286 | 1210 | 11.5494 | 1478 | 339 | 594 | 442 | 442 | 411.6 | 411.6 | 809 | 809 | 1141 | 823 | 803 | 469 | 484 | 1130 | 411.6 | 0 | 0 | 1212 | 1005 | 1005 | 634 | 3.1792 | 127 | 127 | 981 | 840 | 396 |  | 811 | 821 | 1187 | 1219 | 1219 | 1219 | 250
2017 | 23033.2329 | 1210 | 11.4744 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1133 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1212 | 1005 | 1005 | 634 | 3.1585 | 127 | 127 | 981 | 840 | 0 |  | 811 | 821 | 1187 | 1219 | 1219 | 1219 | 0
2018 | 23014.1378 | 1210 | 11.3998 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1212 | 1004 | 1004 | 634 | 3.138 | 127 | 127 | 981 | 840 | 0 |  | 811 | 821 | 1172 | 1219 | 1219 | 1219
2019 | 23054.0433 | 1210 | 11.3257 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1212 | 1004 | 1004 | 634 | 3.1176 | 127 | 127 | 981 | 840 | 0 |  | 831 | 841 | 1172 | 1219 | 1219 | 1219
2020 | 23053.9494 | 1210 | 11.2521 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1212 | 1004 | 1004 | 634 | 3.0973 | 127 | 127 | 981 | 840 | 0 |  | 831 | 841 | 1172 | 1219 | 1219 | 1219
2021 | 23141.8561 | 1298 | 11.1789 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1212 | 1004 | 1004 | 634 | 3.0772 | 127 | 127 | 981 | 840 | 0 |  | 831 | 841 | 1172 | 1219 | 1219 | 1219
2022 | 23227.7635 | 1298 | 11.1063 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 3.0572 | 127 | 127 | 981 | 840 | 0 |  | 831 | 841 | 1172 | 1219 | 1219 | 1219
2023 | 23227.6714 | 1298 | 11.0341 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 3.0373 | 127 | 127 | 981 | 840 | 0 |  | 831 | 841 | 1172 | 1219 | 1219 | 1219
2024 | 23229.5799 | 1300 | 10.9624 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 3.0176 | 127 | 127 | 981 | 840 | 0 |  | 831 | 841 | 1172 | 1219 | 1219 | 1219
2025 | 23229.4891 | 1300 | 10.8911 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.998 | 127 | 127 | 981 | 840 | 0 |  | 831 | 841 | 1172 | 1219 | 1219 | 1219
2026 | 23229.3988 | 1300 | 10.8203 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.9785 | 127 | 127 | 981 | 840 | 0 |  | 831 | 841 | 1172 | 1219 | 1219 | 1219
2027 | 23229.3091 | 1300 | 10.75 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.9591 | 127 | 127 | 981 | 840 | 0 |  | 831 | 841 | 1172 | 1219 | 1219 | 1219
2028 | 23229.22 | 1300 | 10.6801 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.9399 | 127 | 127 | 981 | 840 | 0 |  | 831 | 841 | 1172 | 1219 | 1219 | 1219
2029 | 23229.1315 | 1300 | 10.6107 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.9208 | 127 | 127 | 981 | 840 | 0 |  | 831 | 841 | 1172 | 1219 | 1219 | 1219
2030 | 23229.0435 | 1300 | 10.5417 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.9018 | 127 | 127 | 981 | 840 | 0 |  | 831 | 841 | 1172 | 1219 | 1219 | 1219
2031 | 23228.9561 | 1300 | 10.4732 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.8829 | 127 | 127 | 981 | 840 | 0 |  | 831 | 841 | 1172 | 1219 | 1219 | 1219
2032 | 22397.8693 | 1300 | 10.4051 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.8642 | 127 | 127 | 981 | 840 | 0 |  | 0 | 841 | 1172 | 1219 | 1219 | 1219
2033 | 21556.7831 | 1300 | 10.3375 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.8456 | 127 | 127 | 981 | 840 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2034 | 21556.6974 | 1300 | 10.2703 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.8271 | 127 | 127 | 981 | 840 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2035 | 21556.6122 | 1300 | 10.2035 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.8087 | 127 | 127 | 981 | 840 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2036 | 20575.5277 | 1300 | 10.1372 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.7905 | 127 | 127 | 0 | 840 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2037 | 20575.4436 | 1300 | 10.0713 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.7723 | 127 | 127 | 0 | 840 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2038 | 20575.3601 | 1300 | 10.0059 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.7543 | 127 | 127 | 0 | 840 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2039 | 20575.2772 | 1300 | 9.9408 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.7364 | 127 | 127 | 0 | 840 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2040 | 20575.1948 | 1300 | 9.8762 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.7186 | 127 | 127 | 0 | 840 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2041 | 20575.1129 | 1300 | 9.812 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.7009 | 127 | 127 | 0 | 840 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2042 | 20575.0316 | 1300 | 9.7482 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.6834 | 127 | 127 | 0 | 840 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2043 | 19734.9508 | 1300 | 9.6849 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.6659 | 127 | 127 | 0 | 0 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2044 | 19734.8705 | 1300 | 9.6219 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.6486 | 127 | 127 | 0 | 0 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2045 | 19734.7908 | 1300 | 9.5594 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.6314 | 127 | 127 | 0 | 0 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2046 | 19734.7115 | 1300 | 9.4972 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.6143 | 127 | 127 | 0 | 0 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2047 | 19734.6328 | 1300 | 9.4355 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.5973 | 127 | 127 | 0 | 0 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2048 | 19734.5546 | 1300 | 9.3742 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.5804 | 127 | 127 | 0 | 0 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2049 | 19734.4769 | 1300 | 9.3132 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.5636 | 127 | 127 | 0 | 0 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2050 | 19734.3997 | 1300 | 9.2527 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.547 | 127 | 127 | 0 | 0 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2051 | 19734.323 | 1300 | 9.1926 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.5304 | 127 | 127 | 0 | 0 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2052 | 19734.2468 | 1300 | 9.1328 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.514 | 127 | 127 | 0 | 0 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2053 | 19734.1711 | 1300 | 9.0734 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.4976 | 127 | 127 | 0 | 0 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2054 | 19734.0959 | 1300 | 9.0145 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.4814 | 127 | 127 | 0 | 0 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2055 | 19734.0211 | 1300 | 8.9559 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.4653 | 127 | 127 | 0 | 0 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2056 | 19733.9469 | 1300 | 8.8977 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.4492 | 127 | 127 | 0 | 0 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2057 | 19733.8732 | 1300 | 8.8398 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.4333 | 127 | 127 | 0 | 0 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2058 | 19733.7999 | 1300 | 8.7824 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.4175 | 127 | 127 | 0 | 0 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2059 | 19733.7271 | 1300 | 8.7253 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.4018 | 127 | 127 | 0 | 0 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2060 | 19733.6547 | 1300 | 8.6686 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.3862 | 127 | 127 | 0 | 0 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2061 | 19733.5829 | 1300 | 8.6122 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.3707 | 127 | 127 | 0 | 0 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2062 | 19733.5115 | 1300 | 8.5562 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.3553 | 127 | 127 | 0 | 0 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2063 | 19733.4406 | 1300 | 8.5006 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.34 | 127 | 127 | 0 | 0 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2064 | 19733.3701 | 1300 | 8.4454 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.3247 | 127 | 127 | 0 | 0 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219
2065 | 19733.3001 | 1300 | 8.3905 | 1478 | 364 | 108 | 442 | 442 | 0 | 68.6 | 809 | 809 | 1131 | 823 | 803 | 498 | 498 | 1126 | 0 | 0 | 0 | 1298 | 1004 | 1004 | 634 | 2.3096 | 127 | 127 | 0 | 0 | 0 |  | 0 | 0 | 1172 | 1219 | 1219 | 1219

## Input 4. Firm Purchase-Sale
2016 TYSP Update (ICL retired, only 60 MW ECOGEN, OCEC increase in MWs, and TP6 & 7 delayed to 2031 & 2032)
VI. Firm Capacity Purchases/Sales
Summary of FPL's Firm Capacity Purchases/Sales: Summer MW (for August of Year Shown) | [21 empty] | FOR TYSP ONLY
| I. Purchases from QF's: | [6 empty] | Indicates change in capacity from one year to the next |  |  | II. Purchases from Utilities: |  |  | III. Other Purchases: |  |  |  |  | IV. Sales (not accounted in Load Forecast): |  |  | IV. Unspecified Purchases
Contract Name | Broward South | Broward South | Broward South | Indiantown Cogen., LP | U.S. EcoGen - Clay | U.S. EcoGen -Okeechobee | U.S. EcoGen - Martin |  | QF Totals (MW) |  | SJRPP | Purchases from Utilties (MW) |  | Palm Beach SWA -extension | Palm Beach SWA - additional | Purchases from Others (MW) | Summer Firm Capacity Purchases (MW) | MW Change from Previous Year | Native Load Sale to TECO | Summer Firm Capacity Sales (MW) |  |  |  | # of Other Purchases | 2
Start Date | 1993-01-01 | 1995-01-01 | 1997-01-01 | 1995-12-22 | 2021-01-01 | 2021-01-01 | 2021-01-01 |  |  |  | 1982-04-02 |  |  | 2012-01-01 | 2015-01-01 |  |  |  | 2016-04-01 |  |  |  |  | # of PPA's | 5
End Date | 2026-12-31 | 2026-12-31 | 2026-12-31 | 2019-10-01 | 2049-12-31 | 2049-12-31 | 2049-12-31 |  |  | Year | 2019-11-01 |  | Year | 2034-04-01 | 2034-04-01 |  |  |  | 2016-09-30 |  |  | Year | 1-Year PPA | PPA # | YEAR | MWs
2016 | 1.4 | 1.5 | 0.6 | 330 | 0 | 0 | 0 |  | 333.5 | 2016 | 382 | 382 | 2016 | 40 | 70 | 110 | 825.5 |  | 100 | 100 | 0 | 2016 | 0 | 1 | 2017 | 53
2017 | 1.4 | 1.5 | 0.6 | 330 | 0 | 0 | 0 |  | 333.5 | 2017 | 382 | 382 | 2017 | 40 | 70 | 110 | 825.5 | 0 |  | 0 | 1 | 2017 | 53 | 2 | 2018 | 324
2018 | 1.4 | 1.5 | 0.6 | 330 | 0 | 0 | 0 |  | 333.5 | 2018 | 382 | 382 | 2018 | 40 | 70 | 110 | 825.5 | 0 |  | 0 | 2 | 2018 | 324 | 3 | 2025 | 82
2019 | 1.4 | 1.5 | 0.6 | 330 | 0 | 0 | 0 |  | 333.5 | 2019 | 382 | 382 | 2019 | 40 | 70 | 110 | 825.5 | 0 |  | 0 | 0 | 2019 | 0 | 4 | 2026 | 80
2020 | 1.4 | 1.5 | 0.6 | 0 | 0 | 0 | 0 |  | 3.5 | 2020 | 0 | 0 | 2020 | 40 | 70 | 110 | 113.5 | -712 |  | 0 | 0 | 2020 | 0 | 5 | 2029 | 52
2021 | 1.4 | 1.5 | 0.6 | 0 | 0 | 60 | 0 |  | 63.5 | 2021 | 0 | 0 | 2021 | 40 | 70 | 110 | 173.5 | 60 |  | 0 | 0 | 2021 | 0 | 6
2022 | 1.4 | 1.5 | 0.6 | 0 | 0 | 60 | 0 |  | 63.5 | 2022 | 0 | 0 | 2022 | 40 | 70 | 110 | 173.5 | 0 |  | 0 | 0 | 2022 | 0 | 7
2023 | 1.4 | 1.5 | 0.6 | 0 | 0 | 60 | 0 |  | 63.5 | 2023 | 0 | 0 | 2023 | 40 | 70 | 110 | 173.5 | 0 |  | 0 | 0 | 2023 | 0 | 8
2024 | 1.4 | 1.5 | 0.6 | 0 | 0 | 60 | 0 |  | 63.5 | 2024 | 0 | 0 | 2024 | 40 | 70 | 110 | 173.5 | 0 |  | 0 | 0 | 2024 | 0 | 9
2025 | 1.4 | 1.5 | 0.6 | 0 | 0 | 60 | 0 |  | 63.5 | 2025 | 0 | 0 | 2025 | 40 | 70 | 110 | 173.5 | 0 |  | 0 | 3 | 2025 | 82 | 10
2026 | 1.4 | 1.5 | 0.6 | 0 | 0 | 60 | 0 |  | 63.5 | 2026 | 0 | 0 | 2026 | 40 | 70 | 110 | 173.5 | 0 |  | 0 | 4 | 2026 | 80 | 11
2027 | 0 | 0 | 0 | 0 | 0 | 60 | 0 |  | 60 | 2027 | 0 | 0 | 2027 | 40 | 70 | 110 | 170 | -3.5 |  | 0 | 0 | 2027 | 0 | 12
2028 | 0 | 0 | 0 | 0 | 0 | 60 | 0 |  | 60 | 2028 | 0 | 0 | 2028 | 40 | 70 | 110 | 170 | 0 |  | 0 | 0 | 2028 | 0 | 13
2029 | 0 | 0 | 0 | 0 | 0 | 60 | 0 |  | 60 | 2029 | 0 | 0 | 2029 | 40 | 70 | 110 | 170 | 0 |  | 0 | 5 | 2029 | 52 | 14
2030 | 0 | 0 | 0 | 0 | 0 | 60 | 0 |  | 60 | 2030 | 0 | 0 | 2030 | 40 | 70 | 110 | 170 | 0 |  | 0 | 0 | 2030 | 0 | 15
2031 | 0 | 0 | 0 | 0 | 0 | 60 | 0 |  | 60 | 2031 | 0 | 0 | 2031 | 40 | 70 | 110 | 170 | 0 |  | 0 | 0 | 2031 | 0 | 16
2032 | 0 | 0 | 0 | 0 | 0 | 60 | 0 |  | 60 | 2032 | 0 | 0 | 2032 | 40 | 70 | 110 | 170 | 0 |  | 0 | 0 | 2032 | 0 | 17
2033 | 0 | 0 | 0 | 0 | 0 | 60 | 0 |  | 60 | 2033 | 0 | 0 | 2033 | 40 | 70 | 110 | 170 | 0 |  | 0 | 0 | 2033 | 0 | 18
2034 | 0 | 0 | 0 | 0 | 0 | 60 | 0 |  | 60 | 2034 | 0 | 0 | 2034 | 0 | 0 | 0 | 60 | -110 |  | 0 | 0 | 2034 | 0 | 19
2035 | 0 | 0 | 0 | 0 | 0 | 60 | 0 |  | 60 | 2035 | 0 | 0 | 2035 | 0 | 0 | 0 | 60 | 0 |  | 0 | 0 | 2035 | 0 | 20
2036 | 0 | 0 | 0 | 0 | 0 | 60 | 0 |  | 60 | 2036 | 0 | 0 | 2036 | 0 | 0 | 0 | 60 | 0 |  | 0 | 0 | 2036 | 0
2037 | 0 | 0 | 0 | 0 | 0 | 60 | 0 |  | 60 | 2037 | 0 | 0 | 2037 | 0 | 0 | 0 | 60 | 0 |  | 0 | 0 | 2037 | 0
2038 | 0 | 0 | 0 | 0 | 0 | 60 | 0 |  | 60 | 2038 | 0 | 0 | 2038 | 0 | 0 | 0 | 60 | 0 |  | 0 | 0 | 2038 | 0
2039 | 0 | 0 | 0 | 0 | 0 | 60 | 0 |  | 60 | 2039 | 0 | 0 | 2039 | 0 | 0 | 0 | 60 | 0 |  | 0 | 0 | 2039 | 0
2040 | 0 | 0 | 0 | 0 | 0 | 60 | 0 |  | 60 | 2040 | 0 | 0 | 2040 | 0 | 0 | 0 | 60 | 0 |  | 0 | 0 | 2040 | 0
2041 | 0 | 0 | 0 | 0 | 0 | 60 | 0 |  | 60 | 2041 | 0 | 0 | 2041 | 0 | 0 | 0 | 60 | 0 |  | 0 | 0 | 2041 | 0
2042 | 0 | 0 | 0 | 0 | 0 | 60 | 0 |  | 60 | 2042 | 0 | 0 | 2042 | 0 | 0 | 0 | 60 | 0 |  | 0 | 0 | 2042 | 0
2043 | 0 | 0 | 0 | 0 | 0 | 60 | 0 |  | 60 | 2043 | 0 | 0 | 2043 | 0 | 0 | 0 | 60 | 0 |  | 0 | 0 | 2043 | 0
2044 | 0 | 0 | 0 | 0 | 0 | 60 | 0 |  | 60 | 2044 | 0 | 0 | 2044 | 0 | 0 | 0 | 60 | 0 |  | 0 | 0 | 2044 | 0
2045 | 0 | 0 | 0 | 0 | 0 | 60 | 0 |  | 60 | 2045 | 0 | 0 | 2045 | 0 | 0 | 0 | 60 | 0 |  | 0 | 0 | 2045 | 0
2046 | 0 | 0 | 0 | 0 | 0 | 60 | 0 |  | 60 | 2046 | 0 | 0 | 2046 | 0 | 0 | 0 | 60 | 0 |  | 0 | 0 | 2046 | 0
2047 | 0 | 0 | 0 | 0 | 0 | 60 | 0 |  | 60 | 2047 | 0 | 0 | 2047 | 0 | 0 | 0 | 60 | 0 |  | 0 | 0 | 2047 | 0
2048 | 0 | 0 | 0 | 0 | 0 | 60 | 0 |  | 60 | 2048 | 0 | 0 | 2048 | 0 | 0 | 0 | 60 | 0 |  | 0 | 0 | 2048 | 0
2049 | 0 | 0 | 0 | 0 | 0 | 60 | 0 |  | 60 | 2049 | 0 | 0 | 2049 | 0 | 0 | 0 | 60 | 0 |  | 0 | 0 | 2049 | 0
2050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2050 | 0 | 0 | 2050 | 0 | 0 | 0 | 0 | -60 |  | 0 | 0 | 2050 | 0
2051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2051 | 0 | 0 | 2051 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2051 | 0
2052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2052 | 0 | 0 | 2052 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2052 | 0
2053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2053 | 0 | 0 | 2053 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2053 | 0
2054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2054 | 0 | 0 | 2054 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2054 | 0
2055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2055 | 0 | 0 | 2055 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2055 | 0
2056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2056 | 0 | 0 | 2056 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2056 | 0
2057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2057 | 0 | 0 | 2057 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2057 | 0
2058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2058 | 0 | 0 | 2058 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2058 | 0
2059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2059 | 0 | 0 | 2059 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2059 | 0
2060 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2060 | 0 | 0 | 2060 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2060 | 0
2061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2061 | 0 | 0 | 2061 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2061 | 0
2062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2062 | 0 | 0 | 2062 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2062 | 0
2063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2063 | 0 | 0 | 2063 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2063 | 0
2064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2064 | 0 | 0 | 2064 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2064 | 0
2065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2065 | 0 | 0 | 2065 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2065 | 0

## Output 1. Summary Resource Plan
2016 TYSP Update (ICL retired, only 60 MW ECOGEN, OCEC increase in MWs, and TP6 & 7 delayed to 2031 & 2032)
NOTE: Negative values represents reduction in total system
|  |  |  | MWs |  | capacity. This capacity change is already accounted | [8 empty] | MWs |  |  | MWs
| Reserve | MWs | Gen-Only | (Above)/ |  | for in the RM before unit additions/retirements. | [6 empty] | MWs |  | (Above)/ | MWs |  | (Above)/
| Margin | (Above)/ | RM | Below |  |  | Total |  |  |  |  | Reserve | (Above)/ | Gen-Only | Below | (Above)/ |  | Below
| Before | Below | Before | 10% | Cumulative |  | Capacity |  |  |  | Retired | Margin | Below | RM | 10% | Below |  | 10%
| Additions/ | 20% | Additions/ | Gen-Only | DSM |  | Changes |  | New |  | Unit or | After | 20% | After | Gen-Only | 20% |  | Gen-Only
| Retirements | RM | Retirements | RM | Additions | Unit | of Units | Unit | Unit | Unit | Outages | Changes | RM | Additions | RM | RM |  | RM
Year | (%) | (MW) | (%) | (MW) | (MW) | Modifications | (MW) | Additions | (MW) | Retirements | (MW) | % | (MW) | % | (MW) | (MW) |  | (MW)
2016 | 16.45% | 791.6352 | 7.577% | 585.6266 | 0 |  | 0 | PEEC | 1237 |  | 0 | 21.99% | -445.3648 | 12.7% | -651.3734 | -445.3648 | CHECK | -651.3734 | CHECK
2017 | 18.59% | 316.55 | 9.159% | 204.7118 | 92.3382 | FM 3A&3B CT; FM GT; PFL GT 2; MT 3; MR 3; MR 4; MR 8 | -773 | 223.5 MW Solar; FM 2CT; PFL 5CT; 53 MW PPA | 1786.22 | PFL GT 1; PPE GT; TP 1; Cedar Bay | -1469.2 | 20% | -0.47004 | 10.46% | -112.3082 | -0.47004 | CHECK | -112.3082 | CHECK
2018 | 18.57% | 323.7839 | 8.954% | 257.3977 | 60.3965 | MT 3; SN 4; SN 5; TP 5 | -19 | 324 MW PPA | 324 |  | 0 | 20% | -0.21608 | 10.27% | -66.6023 | -0.21608 | CHECK | -66.6023 | CHECK
2019 | 17.49% | 572.9115 | 7.857% | 533.3369 | 46.2443 | TP 3; TP 4 | 40 | OCEC | 1702 |  | 0 | 24.94% | -1129.0885 | 14.69% | -1168.6631 | -1129.0885 | CHECK | -1168.6631 | CHECK
2020 | 20.42% | -97.667 | 10.44% | -112.1052 | 47.0165 |  | 0 | 300 MW Solar | 156 |  | 0 | 21.1% | -253.667 | 11.06% | -268.1052 | -253.667 | CHECK | -268.1052 | CHECK
2021 | 21.4% | -325.5015 | 11.16% | -293.6619 | 47.7721 | CCEC | 88 | 472 MW Solar | 209.2532 |  | 0 | 22.31% | -534.7546 | 11.99% | -502.9151 | -534.7546 | CHECK | -502.9151 | CHECK
2022 | 21.75% | -408.9102 | 11.34% | -341.2333 | 48.5122 | RBEC | 86 | 471 MW Solar; OCEC Inc MW | 253.8098 |  | 0 | 22.84% | -662.72 | 12.33% | -595.0431 | -662.72 | CHECK | -595.0431 | CHECK
2023 | 21.56% | -368.4497 | 11.05% | -270.9047 | 49.283 |  | 0 | 471 MW Solar | 208.8098 |  | 0 | 22.45% | -577.2596 | 11.86% | -479.7145 | -577.2596 | CHECK | -479.7145 | CHECK
2024 | 20.92% | -219.8198 | 10.37% | -96.829 | 50.1527 | CCEC | 2 |  | 0 |  | 0 | 20.92% | -219.8198 | 10.37% | -96.829 | -219.8198 | CHECK | -96.829 | CHECK
2025 | 19.2% | 193.7759 | 8.731% | 337.3303 | 49.8178 |  | 0 | Battery; 82 MW PPA | 337.35 |  | 0 | 20.59% | -143.5741 | 10% | -0.01975 | -143.5741 | CHECK | -0.01975 | CHECK
2026 | 18.07% | 475.3542 | 7.675% | 629.3941 | 50 |  | 0 | Battery; 80 MW PPA | 630 |  | 0 | 20.63% | -154.6458 | 10% | -0.60585 | -154.6458 | CHECK | -0.60585 | CHECK
2027 | 17.67% | 588.7439 | 7.314% | 743.022 | 50 |  | 0 | CC | 1751 |  | 0 | 24.61% | -1162.2561 | 13.64% | -1007.978 | -1162.2561 | CHECK | -1007.978 | CHECK
2028 | 22.13% | -548.1116 | 11.38% | -389.7841 | 50 |  | 0 |  | 0 |  | 0 | 22.13% | -548.1116 | 11.38% | -389.7841 | -548.1116 | CHECK | -389.7841 | CHECK
2029 | 19.65% | 90.7262 | 9.128% | 251.0448 | 50 |  | 0 | Battery; 52 MW PPA | 252 |  | 0 | 20.61% | -161.2738 | 10% | -0.95525 | -161.2738 | CHECK | -0.95525 | CHECK
2030 | 17.97% | 544.8644 | 7.599% | 705.8982 | 50 |  | 0 | Battery | 664.7 |  | 0 | 20.45% | -119.8356 | 9.86% | 41.1982 | -119.8356 | CHECK | 41.1982 | CHECK
2031 | 18.15% | 505.4662 | 7.946% | 614.6176 | 0 |  | 0 | 615 MW Eq Filler | 614.6176 |  | 0 | 20.4% | -109.1514 | 10% | 0 | -109.1514 | CHECK | 0 | CHECK
2032 | 17.96% | 568.2244 | 7.962% | 621.1532 | 0 |  | 0 | 2 Filler | 1751 | TP 3 | -831 | 21.26% | -351.7756 | 10.98% | -298.8468 | -351.7756 | CHECK | -298.8468 | CHECK
2033 | 18.97% | 293.9881 | 9.054% | 293.3279 | 0 |  | 0 | 2 Filler | 1751 | TP 4 | -841 | 22.17% | -616.0119 | 11.99% | -616.6721 | -616.0119 | CHECK | -616.6721 | CHECK
2034 | 19.74% | 75.469 | 9.916% | 26.576 | 0 |  | 0 | 1 Filler | 875.5 |  | 0 | 22.77% | -800.031 | 12.7% | -848.924 | -800.031 | CHECK | -848.924 | CHECK
2035 | 20.72% | -211.5429 | 10.97% | -309.2533 | 0 |  | 0 |  | 0 |  | 0 | 20.72% | -211.5429 | 10.97% | -309.2533 | -211.5429 | CHECK | -309.2533 | CHECK
2036 | 18.76% | 370.6262 | 9.308% | 224.6242 | 0 |  | 0 | 2 Filler | 1751 | SL 1 | -981 | 21.34% | -399.3738 | 11.68% | -545.3758 | -399.3738 | CHECK | -545.3758 | CHECK
2037 | 19.5% | 152.9416 | 10.12% | -38.8647 | 0 |  | 0 | 1 Filler | 875.5 |  | 0 | 22.38% | -722.5584 | 12.78% | -914.3647 | -722.5584 | CHECK | -914.3647 | CHECK
2038 | 20.49% | -149.7213 | 11.16% | -389.0429 | 0 |  | 0 |  | 0 |  | 0 | 20.49% | -149.7213 | 11.16% | -389.0429 | -149.7213 | CHECK | -389.0429 | CHECK
2039 | 18.64% | 424.6105 | 9.594% | 137.6484 | 0 |  | 0 | 1 Filler | 875.5 |  | 0 | 21.44% | -450.8895 | 12.18% | -737.8516 | -450.8895 | CHECK | -737.8516 | CHECK
2040 | 19.58% | 133.1314 | 10.59% | -202.2792 | 0 |  | 0 | 1 Filler | 875.5 |  | 0 | 22.34% | -742.3686 | 13.14% | -1077.7792 | -742.3686 | CHECK | -1077.7792 | CHECK
2041 | 20.84% | -271.2138 | 11.86% | -645.6682 | 0 |  | 0 |  | 0 |  | 0 | 20.84% | -271.2138 | 11.86% | -645.6682 | -271.2138 | CHECK | -645.6682 | CHECK
2042 | 19.38% | 200.7699 | 10.61% | -212.7981 | 0 |  | 0 | 1 Filler | 875.5 |  | 0 | 22.07% | -674.7301 | 13.1% | -1088.2981 | -674.7301 | CHECK | -1088.2981 | CHECK
2043 | 20.61% | -201.9163 | 11.84% | -654.6676 | 0 |  | 0 | 1 Filler | 875.5 | SL 2 | -840 | 20.72% | -237.4163 | 11.94% | -690.1676 | -237.4163 | CHECK | -690.1676 | CHECK
2044 | 19.29% | 236.2291 | 10.71% | -255.7755 | 0 |  | 0 | 1 Filler | 875.5 |  | 0 | 21.92% | -639.2709 | 13.15% | -1131.2755 | -639.2709 | CHECK | -1131.2755 | CHECK
2045 | 20.49% | -164.7926 | 11.92% | -696.1207 | 0 |  | 0 |  | 0 |  | 0 | 20.49% | -164.7926 | 11.92% | -696.1207 | -164.7926 | CHECK | -696.1207 | CHECK
2046 | 19.09% | 310.5199 | 10.71% | -260.2019 | 0 |  | 0 | 1 Filler | 875.5 |  | 0 | 21.66% | -564.9801 | 13.09% | -1135.7019 | -564.9801 | CHECK | -1135.7019 | CHECK

## Output 1a. Simplified Summary
THIS SHEET IS NOT PROTECTED
UPLAN UNIT ADDITIONS
2016 TYSP Update (ICL retired, only 60 MW ECOGEN, OCEC increase in MWs, and TP6 & 7 delayed to 2031 & 2032)
MWs
[6 empty] | MWs |  | (Above)/
[5 empty] | Reserve | (Above)/ | Gen-Only | Below
|  |  |  | Retired | Margin | Below | RM | 10%
|  | New |  | Unit or | After | 20% | After | Gen-Only
| Unit | Unit | Unit | Outages | Changes | RM | Additions | RM
Year | Additions | (MW) | Retirements | (MW) | % | (MW) | % | (MW)
2016 | PEEC | 1237 |  | 0 | 21.99% | -445.3648 | 12.7% | -651.3734
2017 | 223.5 MW Solar; FM 2CT; PFL 5CT; 53 MW PPA | 1786.22 | PFL GT 1; PPE GT; TP 1; Cedar Bay | -1469.2 | 20% | -0.47004 | 10.46% | -112.3082
2018 | 324 MW PPA | 324 |  | 0 | 20% | -0.21608 | 10.27% | -66.6023
2019 | OCEC | 1702 |  | 0 | 24.94% | -1129.0885 | 14.69% | -1168.6631
2020 | 300 MW Solar | 156 |  | 0 | 21.1% | -253.667 | 11.06% | -268.1052
2021 | 472 MW Solar | 209.2532 |  | 0 | 22.31% | -534.7546 | 11.99% | -502.9151
2022 | 471 MW Solar; OCEC Inc MW | 253.8098 |  | 0 | 22.84% | -662.72 | 12.33% | -595.0431
2023 | 471 MW Solar | 208.8098 |  | 0 | 22.45% | -577.2596 | 11.86% | -479.7145
2024 |  | 0 |  | 0 | 20.92% | -219.8198 | 10.37% | -96.829
2025 | Battery; 82 MW PPA | 337.35 |  | 0 | 20.59% | -143.5741 | 10% | -0.01975
2026 | Battery; 80 MW PPA | 630 |  | 0 | 20.63% | -154.6458 | 10% | -0.60585
2027 | CC | 1751 |  | 0 | 24.61% | -1162.2561 | 13.64% | -1007.978
2028 |  | 0 |  | 0 | 22.13% | -548.1116 | 11.38% | -389.7841
2029 | Battery; 52 MW PPA | 252 |  | 0 | 20.61% | -161.2738 | 10% | -0.95525
2030 | Battery | 664.7 |  | 0 | 20.45% | -119.8356 | 9.86% | 41.1982
2031 | 615 MW Eq Filler | 614.6176 |  | 0 | 20.4% | -109.1514 | 10% | 0
2032 | 2 Filler | 1751 | TP 3 | -831 | 21.26% | -351.7756 | 10.98% | -298.8468
2033 | 2 Filler | 1751 | TP 4 | -841 | 22.17% | -616.0119 | 11.99% | -616.6721
2034 | 1 Filler | 875.5 |  | 0 | 22.77% | -800.031 | 12.7% | -848.924
2035 |  | 0 |  | 0 | 20.72% | -211.5429 | 10.97% | -309.2533
2036 | 2 Filler | 1751 | SL 1 | -981 | 21.34% | -399.3738 | 11.68% | -545.3758
2037 | 1 Filler | 875.5 |  | 0 | 22.38% | -722.5584 | 12.78% | -914.3647
2038 |  | 0 |  | 0 | 20.49% | -149.7213 | 11.16% | -389.0429
2039 | 1 Filler | 875.5 |  | 0 | 21.44% | -450.8895 | 12.18% | -737.8516
2040 | 1 Filler | 875.5 |  | 0 | 22.34% | -742.3686 | 13.14% | -1077.7792
2041 |  | 0 |  | 0 | 20.84% | -271.2138 | 11.86% | -645.6682
2042 | 1 Filler | 875.5 |  | 0 | 22.07% | -674.7301 | 13.1% | -1088.2981
2043 | 1 Filler | 875.5 | SL 2 | -840 | 20.72% | -237.4163 | 11.94% | -690.1676
2044 | 1 Filler | 875.5 |  | 0 | 21.92% | -639.2709 | 13.15% | -1131.2755
2045 |  | 0 |  | 0 | 20.49% | -164.7926 | 11.92% | -696.1207
2046 | 1 Filler | 875.5 |  | 0 | 21.66% | -564.9801 | 13.09% | -1135.7019

## Output 2. TYSP Schedule 7.1
Schedule 7.1
Forecast of Capacity, Demand, and Scheduled
Maintenance At Time Of Summer Peak
-1 | -2 | -3 | -4 | -5 | -6 | -7 | -8 | -9 | -10 | -11 | -12 | -13 | -14 | -15 | -16
[5 empty] | Total |  |  | Firm | Total |  |  | Total |  | Generation Only
| Firm | Firm | Firm |  | Firm | Total |  | Summer | Reserve |  |  | Reserve |  | Reserve
| Installed | Capacity | Capacity | Firm | Capacity | Peak |  | Peak | Margin Before |  | Scheduled | Margin After |  | Margin After
August of | Capacity | Import | Export | QF | Available | Demand | DSM | Demand | Maintenance |  | Maintenance | Maintenance |  | Maintenance
Year | MW | MW | MW | MW | MW | MW | MW | MW | MW | % of Peak | MW | MW | % of Peak | MW | % of Peak
2016 | 26512.5286 | 492 | 100 | 333.5 | 27238.0286 | 24169.6865 | 1842.4667 | 22327.2199 | 4910.8088 | 21.9947 | 0 | 4910.8088 | 21.9947 | 3068.3421 | 12.695
2017 | 26003.4529 | 545 | 0 | 333.5 | 26881.9529 | 24336.0406 | 1934.8049 | 22401.2357 | 4480.7172 | 20.0021 | 0 | 4480.7172 | 20.0021 | 2545.9123 | 10.4615
2018 | 25984.0091 | 816 | 0 | 333.5 | 27133.5091 | 24606.279 | 1995.2014 | 22611.0775 | 4522.4316 | 20.001 | 0 | 4522.4316 | 20.001 | 2527.2302 | 10.2707
2019 | 27725.567 | 492 | 0 | 333.5 | 28551.067 | 24893.0945 | 2041.4457 | 22851.6488 | 5699.4183 | 24.9409 | 0 | 5699.4183 | 24.9409 | 3657.9726 | 14.6947
2020 | 27881.1266 | 110 | 0 | 3.5 | 27994.6266 | 25205.9285 | 2088.4622 | 23117.4663 | 4877.1602 | 21.0973 | 0 | 4877.1602 | 21.0973 | 2788.698 | 11.0637
2021 | 28177.4729 | 110 | 0 | 63.5 | 28350.9729 | 25316.4163 | 2136.2343 | 23180.1819 | 5170.791 | 22.3069 | 0 | 5170.791 | 22.3069 | 3034.5567 | 11.9865
2022 | 28515.7513 | 110 | 0 | 63.5 | 28689.2513 | 25540.1892 | 2184.7465 | 23355.4427 | 5333.8086 | 22.8375 | 0 | 5333.8086 | 22.8375 | 3149.0621 | 12.3298
2023 | 28722.4081 | 110 | 0 | 63.5 | 28895.9081 | 25832.9033 | 2234.0295 | 23598.8738 | 5297.0343 | 22.4461 | 0 | 5297.0343 | 22.4461 | 3063.0048 | 11.857
2024 | 28721.6354 | 110 | 0 | 63.5 | 28895.1354 | 26180.2785 | 2284.1822 | 23896.0963 | 4999.0391 | 20.9199 | 0 | 4999.0391 | 20.9199 | 2714.8569 | 10.3699
2025 | 28974.2214 | 192 | 0 | 63.5 | 29229.7214 | 26572.456 | 2334 | 24238.456 | 4991.2654 | 20.5923 | 0 | 4991.2654 | 20.5923 | 2657.2654 | 10.0001
Col. (2) represents capacity additions and changes projected to be in-service by June 1st. These MW are generally considered to be available to meet summer
peak loads which are forecasted to occur during August of the year indicated.
Col. (6) = Col.(2) + Col.(3) - Col(4) + Col(5).
Col.(7) reflects the 2015 load forecast without incremental DSM or cumulative load management. 2015 load is an actual load value.
Col.(8) represents cumulative load management capability, plus incremental conservation and load management, from 9/2015-on intended for use with the
2015 load forecast.
Col.(10) = Col.(6) - Col.(9)
Col.(11) = Col.(10) / Col.(9)
Col.(12) indicates the capacity of units projected to be out-of-service for planned maintenance during the summer peak period.
Col.(13) = Col.(10) - Col.(12)
Col.(14) = Col.(13) / Col.(9)
Col.(15) = Col.(6) - Col.(7) - Col.(12)
Col.(16) = Col.(15) / Col.(7)

## Output 2a.TYSP Schedule 7.1 Ext
Schedule 7.1
Forecast of Capacity, Demand, and Scheduled
Maintenance At Time Of Summer Peak
-1 | -2 | -3 | -4 | -5 | -6 | -7 | -8 | -9 | -10 | -11 | -12 | -13 | -14 | -15 | -16
[5 empty] | Total |  |  | Firm | Total |  |  | Total |  | Generation Only
| Firm | Firm | Firm |  | Firm | Total |  | Summer | Reserve |  |  | Reserve |  | Reserve
| Installed | Capacity | Capacity | Firm | Capacity | Peak |  | Peak | Margin Before |  | Scheduled | Margin After |  | Margin After
August of | Capacity | Import | Export | QF | Available | Demand | DSM | Demand | Maintenance |  | Maintenance | Maintenance |  | Maintenance
Year | MW | MW | MW | MW | MW | MW | MW | MW | MW | % of Peak | MW | MW | % of Peak | MW | % of Peak
2016 | 26512.5286 | 492 | 100 | 333.5 | 27238.0286 | 24169.6865 | 1842.4667 | 22327.2199 | 4910.8088 | 21.9947 | 0 | 4910.8088 | 21.9947 | 3068.3421 | 12.695
2017 | 26003.4529 | 545 | 0 | 333.5 | 26881.9529 | 24336.0406 | 1934.8049 | 22401.2357 | 4480.7172 | 20.0021 | 0 | 4480.7172 | 20.0021 | 2545.9123 | 10.4615
2018 | 25984.0091 | 816 | 0 | 333.5 | 27133.5091 | 24606.279 | 1995.2014 | 22611.0775 | 4522.4316 | 20.001 | 0 | 4522.4316 | 20.001 | 2527.2302 | 10.2707
2019 | 27725.567 | 492 | 0 | 333.5 | 28551.067 | 24893.0945 | 2041.4457 | 22851.6488 | 5699.4183 | 24.9409 | 0 | 5699.4183 | 24.9409 | 3657.9726 | 14.6947
2020 | 27881.1266 | 110 | 0 | 3.5 | 27994.6266 | 25205.9285 | 2088.4622 | 23117.4663 | 4877.1602 | 21.0973 | 0 | 4877.1602 | 21.0973 | 2788.698 | 11.0637
2021 | 28177.4729 | 110 | 0 | 63.5 | 28350.9729 | 25316.4163 | 2136.2343 | 23180.1819 | 5170.791 | 22.3069 | 0 | 5170.791 | 22.3069 | 3034.5567 | 11.9865
2022 | 28515.7513 | 110 | 0 | 63.5 | 28689.2513 | 25540.1892 | 2184.7465 | 23355.4427 | 5333.8086 | 22.8375 | 0 | 5333.8086 | 22.8375 | 3149.0621 | 12.3298
2023 | 28722.4081 | 110 | 0 | 63.5 | 28895.9081 | 25832.9033 | 2234.0295 | 23598.8738 | 5297.0343 | 22.4461 | 0 | 5297.0343 | 22.4461 | 3063.0048 | 11.857
2024 | 28721.6354 | 110 | 0 | 63.5 | 28895.1354 | 26180.2785 | 2284.1822 | 23896.0963 | 4999.0391 | 20.9199 | 0 | 4999.0391 | 20.9199 | 2714.8569 | 10.3699
2025 | 28974.2214 | 192 | 0 | 63.5 | 29229.7214 | 26572.456 | 2334 | 24238.456 | 4991.2654 | 20.5923 | 0 | 4991.2654 | 20.5923 | 2657.2654 | 10.0001
2026 | 29521.4659 | 190 | 0 | 63.5 | 29774.9659 | 27067.6001 | 2384 | 24683.6001 | 5091.3659 | 20.6265 | 0 | 5091.3659 | 20.6265 | 2707.3659 | 10.0022
2027 | 31269.7191 | 110 | 0 | 60 | 31439.7191 | 27665.2192 | 2434 | 25231.2192 | 6208.4999 | 24.6064 | 0 | 6208.4999 | 24.6064 | 3774.4999 | 13.6435
2028 | 31266.9808 | 110 | 0 | 60 | 31436.9808 | 28224.7243 | 2484 | 25740.7243 | 5696.2565 | 22.1294 | 0 | 5696.2565 | 22.1294 | 3212.2565 | 11.381
2029 | 31464.2511 | 162 | 0 | 60 | 31686.2511 | 28804.8144 | 2534 | 26270.8144 | 5415.4367 | 20.6139 | 0 | 5415.4367 | 20.6139 | 2881.4367 | 10.0033
2030 | 32126.2298 | 110 | 0 | 60 | 32296.2298 | 29397.6618 | 2584 | 26813.6618 | 5482.568 | 20.4469 | 0 | 5482.568 | 20.4469 | 2898.568 | 9.8599
2031 | 32738.1346 | 110 | 0 | 60 | 32908.1346 | 29916.486 | 2584 | 27332.486 | 5575.6486 | 20.3993 | 0 | 5575.6486 | 20.3993 | 2991.6486 | 10
2032 | 33655.4302 | 110 | 0 | 60 | 33825.4302 | 30478.7122 | 2584 | 27894.7122 | 5930.718 | 21.2611 | 0 | 5930.718 | 21.2611 | 3346.718 | 10.9805
2033 | 34562.7343 | 110 | 0 | 60 | 34732.7343 | 31014.602 | 2584 | 28430.602 | 6302.1323 | 22.1667 | 0 | 6302.1323 | 22.1667 | 3718.1323 | 11.9883
2034 | 35435.5468 | 0 | 0 | 60 | 35495.5468 | 31496.9298 | 2584 | 28912.9298 | 6582.617 | 22.767 | 0 | 6582.617 | 22.767 | 3998.617 | 12.6953
2035 | 35432.8676 | 0 | 0 | 60 | 35492.8676 | 31985.1039 | 2584 | 29401.1039 | 6091.7637 | 20.7195 | 0 | 6091.7637 | 20.7195 | 3507.7637 | 10.9669
2036 | 36200.1968 | 0 | 0 | 60 | 36260.1968 | 32468.0191 | 2584 | 29884.0191 | 6376.1777 | 21.3364 | 0 | 6376.1777 | 21.3364 | 3792.1777 | 11.6797
2037 | 37073.0342 | 0 | 0 | 60 | 37133.0342 | 32926.0632 | 2584 | 30342.0632 | 6790.971 | 22.3814 | 0 | 6790.971 | 22.3814 | 4206.971 | 12.777
2038 | 37070.38 | 0 | 0 | 60 | 37130.38 | 33401.2155 | 2584 | 30817.2155 | 6313.1644 | 20.4858 | 0 | 6313.1644 | 20.4858 | 3729.1644 | 11.1648
2039 | 37943.234 | 0 | 0 | 60 | 38003.234 | 33877.6204 | 2584 | 31293.6204 | 6709.6136 | 21.4408 | 0 | 6709.6136 | 21.4408 | 4125.6136 | 12.178
2040 | 38816.0962 | 0 | 0 | 60 | 38876.0962 | 34362.1064 | 2584 | 31778.1064 | 7097.9898 | 22.3361 | 0 | 7097.9898 | 22.3361 | 4513.9898 | 13.1365
2041 | 38813.4666 | 0 | 0 | 60 | 38873.4666 | 34752.544 | 2584 | 32168.544 | 6704.9226 | 20.8431 | 0 | 6704.9226 | 20.8431 | 4120.9226 | 11.8579
2042 | 39686.3452 | 0 | 0 | 60 | 39746.3452 | 35143.6793 | 2584 | 32559.6793 | 7186.666 | 22.0723 | 0 | 7186.666 | 22.0723 | 4602.666 | 13.0967
2043 | 39719.232 | 0 | 0 | 60 | 39779.232 | 35535.5131 | 2584 | 32951.5131 | 6827.7189 | 20.7205 | 0 | 6827.7189 | 20.7205 | 4243.7189 | 11.9422
2044 | 40592.1269 | 0 | 0 | 60 | 40652.1269 | 35928.0467 | 2584 | 33344.0467 | 7308.0802 | 21.9172 | 0 | 7308.0802 | 21.9172 | 4724.0802 | 13.1487
2045 | 40589.5299 | 0 | 0 | 60 | 40649.5299 | 36321.2811 | 2584 | 33737.2811 | 6912.2488 | 20.4885 | 0 | 6912.2488 | 20.4885 | 4328.2488 | 11.9166
2046 | 41462.4409 | 0 | 0 | 60 | 41522.4409 | 36715.2173 | 2584 | 34131.2173 | 7391.2236 | 21.6553 | 0 | 7391.2236 | 21.6553 | 4807.2236 | 13.0933
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!

## Output 3. TYSP Table I.B.1
Summary of FPL's Firm Capacity Purchases: Summer MW (for August of Year Shown)
I. Purchases from QF's:
| Cogeneration Small Power | Contract | Contract | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36
| Production Facilities | Start Date | End Date | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
1 | Broward South | 1993-01-01 | 2026-12-31 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Broward South | 1995-01-01 | 2026-12-31 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Broward South | 1997-01-01 | 2026-12-31 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Indiantown Cogen., LP | 1995-12-22 | 2019-10-01 | 330 | 330 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | U.S. EcoGen - Clay | 2021-01-01 | 2049-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | U.S. EcoGen -Okeechobee | 2021-01-01 | 2049-12-31 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 0 | 0
7 | U.S. EcoGen - Martin | 2021-01-01 | 2049-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | QF Purchases Sub Total: | 333.5 | 333.5 | 333.5 | 333.5 | 3.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 0 | 0
| II. Purchases from Utilities: | Contract | Contract
|  | Start Date | End Date | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
1 | SJRPP | 1982-04-02 | 2019-11-01 | 382 | 382 | 382 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Utility Purchases Sub Total: | 382 | 382 | 382 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total of QF and Utility Purchases = |  |  | 715.5 | 715.5 | 715.5 | 715.5 | 3.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 0 | 0
| III. Other Purchases: | Contract | Contract
|  | Start Date | End Date | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
1 | Palm Beach SWA -extension | 2012-01-01 | 2034-04-01 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Palm Beach SWA - additional | 2015-01-01 | 2034-04-01 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Unspecified Purchase | 4/1/2017 | 9/30/2017 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Unspecified Purchase | 4/1/2018 | 9/30/2018 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Unspecified Purchase | 4/1/2025 | 9/30/2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Unspecified Purchase | 4/1/2026 | 9/30/2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other Purchases Sub Total: | 110 | 163 | 434 | 110 | 110 | 110 | 110 | 110 | 110 | 192 | 190 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total "Non-QF" Purchase Sub-Total = |  |  | 492 | 545 | 816 | 492 | 110 | 110 | 110 | 110 | 110 | 192 | 190 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
|  |  | Summer Firm Capacity Purchases Total MW: | 825.5 | 878.5 | 1149.5 | 825.5 | 113.5 | 173.5 | 173.5 | 173.5 | 173.5 | 255.5 | 253.5 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 0 | 0
|  |  | MW change from previous year: | --- | 53 | 271 | -324 | -712 | 60 | 0 | 0 | 0 | 82 | -2 | -83.5 | 0 | 0 | 0 | 0 | 0 | 0 | -110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -60 | 0
Formulas:
Contract = IF([II. Purchases from Utilities:]="Unspecified Purchase","1/1/"&VLOOKUP(A31-No_Other_PPA,'Input 4. Firm Purchase-Sale'!$AQ10:AS29,2),IF('Input 4. Firm Purchase-Sale'!Z$8="","",'Input 4. Firm Purchase-Sale'!Z$8))
Contract = IF([II. Purchases from Utilities:]="Unspecified Purchase","1/1/"&VLOOKUP(A32-No_Other_PPA,'Input 4. Firm Purchase-Sale'!$AQ10:AS29,2),IF('Input 4. Firm Purchase-Sale'!AA$8="","",'Input 4. Firm Purchase-Sale'!AA$8))

## Output 4. EGEAS RM
Instructions: | 1. Complete Input 1, 3, and 4 Tabs
2. Remove any units from Input 2 that are not "Set/Committed" (Ex. 2019 Unit). In other words, change the
inputs to the large filler units, equalizing filler and small filler to years beyond EGEAS study period
3. Press "Easy Button" on Input 2 tab
RM needed to
match Gen Only need
Forecast
of
Summer
Res.Margins
(%)
| 2016 | 20%
| 2017 | 20%
| 2018 | 20%
| 2019 | 20%
| 2020 | 20%
| 2021 | 20%
| 2022 | 20%
| 2023 | 20%
| 2024 | 20%
| 2025 | 20%
| 2026 | 20%
| 2027 | 20%
| 2028 | 20%
| 2029 | 20%
| 2030 | 20.6%
| 2031 | 20%
| 2032 | 20%
| 2033 | 20%
| 2034 | 20%
| 2035 | 20%
| 2036 | 20%
| 2037 | 20%
| 2038 | 20%
| 2039 | 20%
| 2040 | 20%
| 2041 | 20%
| 2042 | 20%
| 2043 | 20%
| 2044 | 20%
| 2045 | 20%
| 2046 | 20%
| 2047 | 20%
| 2048 | 20%
| 2049 | 20%
| 2050 | 20%
| 2051 | 20%
| 2052 | 20%
| 2053 | 20%
| 2054 | 20%
| 2055 | 20%
| 2056 | 20%
| 2057 | 20%
| 2058 | 20%
| 2059 | 20%
| 2060 | 20%
| 2061 | 20%
| 2062 | 20%
| 2063 | 20%
| 2064 | 20%
| 2065 | 20%